## NI Signals from Patch Panel
SVT Hardware Interlock Connections / Signals from Patch Panel Blocks
2015-08-13
Category | # | SVT Region | SVT Sector / Module | NI cRio Module Type | cRio Slot # | cRio Channel + | cRio Connector Pin | Hardware Interlock Cable ID | Patch Panel Block Number | Block Pin # | EPICS SC Cable ID | VME Slot # | VME Board Type | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Main Control System Signal Name | Comments
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0+ | HFCB_R1_M1 | 1 | 1 | HFCB_R1_M1 | 2 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0- |  | 1 | 14 | HFCB_R1_M1 | 2 | V450 | J1 | 14 | CH 0-
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1+ | HFCB_R2_M1 | 3 | 5 | HFCB_R2_M1 | 3 | V450 | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1- |  | 3 | 18 | HFCB_R2_M1 | 3 | V450 | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2+ | HFCB_R3_M1 | 7 | 1 | HFCB_R3_M1 | 5 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2- |  | 7 | 14 | HFCB_R3_M1 | 5 | V450 | J1 | 14 | CH 0-
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3+ | HFCB_R4_M1 | 13 | 1 | HFCB_R4_M1 | 8 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3- |  | 13 | 14 | HFCB_R4_M1 | 8 | V450 | J1 | 14 | CH 0-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | EX0 | DET_INT_TEMP_SB3 | 3 | 11 | RTD_B3_T2 | 3 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0+ |  | 3 | 24 | RTD_B3_T2 | 3 | V450 | J1 | 24 | RtdB E-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0- |  | 3 | 12 | RTD_B3_T2 | 3 | V450 | J1 | 12 | RtdB S+
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | COM |  | 3 | 25 | RTD_B3_T2 | 3 | V450 | J1 | 25 | RtdB S-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | EX1 | DET_INT_TEMP_SB6 | 6 | 11 | RTD_B6_T2 | 4 | V450 | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1+ |  | 6 | 24 | RTD_B6_T2 | 4 | V450 | J2 | 24 | RtdD E-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1- |  | 6 | 12 | RTD_B6_T2 | 4 | V450 | J2 | 12 | RtdD S+
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | COM |  | 6 | 25 | RTD_B6_T2 | 4 | V450 | J2 | 25 | RtdD S-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | EX2 | DET_INT_TEMP_SB9 | 9 | 11 | RTD_B9_T2 | 6 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2+ |  | 9 | 24 | RTD_B9_T2 | 6 | V450 | J1 | 24 | RtdB E-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2- |  | 9 | 12 | RTD_B9_T2 | 6 | V450 | J1 | 12 | RtdB S+
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | COM |  | 9 | 25 | RTD_B9_T2 | 6 | V450 | J1 | 25 | RtdB S-
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI0 (+) | DET_INT_HUM_SB3 | 19 | 6 |  | 11 | V450 | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI8 (-) |  | 19 | 19 |  | 11 | V450 | J1 | 19 | CH 5-
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI1 (+) | DET_INT_HUM_SB6 | 20 | 4 |  | 11 | V450 | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI9 (-) |  | 20 | 17 |  | 11 | V450 | J2 | 17 | CH 11-
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI2 (+) | DET_INT_HUM_SB9 | 22 | 6 |  | 12 | V450 | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI10 (-) |  | 22 | 19 |  | 12 | V450 | J2 | 19 | CH 13-
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0+ | COOL_FLOW_R1_R3 | 21 | 4 |  | 12 | V450 | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R1-R3)
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0- |  | 21 | 17 |  | 12 | V450 | J1 | 17 | CH 3-
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1+ | COOL_FLOW_R1_R4 | 21 | 5 |  | 12 | V450 | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R4)
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1- |  | 21 | 18 |  | 12 | V450 | J1 | 18 | CH 4-
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2+ | COOL_TEMP | 21 | 2 |  | 12 | V450 | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2- |  | 21 | 15 |  | 12 | V450 | J1 | 15 | CH 1-

## NI Signals
SVT Hardware Interlock Signals by cRio Channels
2015-08-13
Category | # | SVT Region | SVT Sector / Module | NI cRio Module Type | cRio Slot # | cRio Channel + | cRio Connector Pin | Hardware Interlock Cable ID | Interlock System Cable Asssembly Type | Patch Panel Block Number | Block Pin # | EPICS SC Cable ID | VME Slot # | VME Board Type | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Main Control System Signal Name | Comments
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0+ | HFCB_R1_M1 | HFCB Temperature Cable Assemblies | 1 | 1 | HFCB_R1_M1 | 2 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0- |  |  | 1 | 14 | HFCB_R1_M1 | 2 | V450 | J1 | 14 | CH 0-
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1+ | HFCB_R2_M1 | HFCB Temperature Cable Assemblies | 3 | 5 | HFCB_R2_M1 | 3 | V450 | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1- |  |  | 3 | 18 | HFCB_R2_M1 | 3 | V450 | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2+ | HFCB_R3_M1 | HFCB Temperature Cable Assemblies | 7 | 1 | HFCB_R3_M1 | 5 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2- |  |  | 7 | 14 | HFCB_R3_M1 | 5 | V450 | J1 | 14 | CH 0-
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3+ | HFCB_R4_M1 | HFCB Temperature Cable Assemblies | 13 | 1 | HFCB_R4_M1 | 8 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3- |  |  | 13 | 14 | HFCB_R4_M1 | 8 | V450 | J1 | 14 | CH 0-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | EX0 | DET_INT_TEMP_SB3 | Detector Temperature Cable Extension Assemblies | 3 | 11 | RTD_B3_T2 | 3 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0+ |  |  | 3 | 24 | RTD_B3_T2 | 3 | V450 | J1 | 24 | RtdB E-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0- |  |  | 3 | 12 | RTD_B3_T2 | 3 | V450 | J1 | 12 | RtdB S+
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | COM |  |  | 3 | 25 | RTD_B3_T2 | 3 | V450 | J1 | 25 | RtdB S-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | EX1 | DET_INT_TEMP_SB6 | Detector Temperature Cable Extension Assemblies | 6 | 11 | RTD_B6_T2 | 4 | V450 | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1+ |  |  | 6 | 24 | RTD_B6_T2 | 4 | V450 | J2 | 24 | RtdD E-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1- |  |  | 6 | 12 | RTD_B6_T2 | 4 | V450 | J2 | 12 | RtdD S+
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | COM |  |  | 6 | 25 | RTD_B6_T2 | 4 | V450 | J2 | 25 | RtdD S-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | EX2 | DET_INT_TEMP_SB9 | Detector Temperature Cable Extension Assemblies | 9 | 11 | RTD_B9_T2 | 6 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2+ |  |  | 9 | 24 | RTD_B9_T2 | 6 | V450 | J1 | 24 | RtdB E-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2- |  |  | 9 | 12 | RTD_B9_T2 | 6 | V450 | J1 | 12 | RtdB S+
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | COM |  |  | 9 | 25 | RTD_B9_T2 | 6 | V450 | J1 | 25 | RtdB S-
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | EX0 | DET_AMB_TEMP_T1 | Ambient Temperature Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Environmental Temperature Sensor - T1
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | RTD0+ |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | RTD0- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | COM |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | EX1 | DET_AMB_TEMP_T2 | Ambient Temperature Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Environmental Temperature Sensor - T2
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | RTD1+ |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | RTD1- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | COM |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI0 (+) | DET_INT_HUM_SB3 | Detector Humidity Cable Extension Assemblies | 19 | 6 |  | 11 | V450 | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI8 (-) |  |  | 19 | 19 |  | 11 | V450 | J1 | 19 | CH 5-
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI1 (+) | DET_INT_HUM_SB6 | Detector Humidity Cable Extension Assemblies | 20 | 4 |  | 11 | V450 | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI9 (-) |  |  | 20 | 17 |  | 11 | V450 | J2 | 17 | CH 11-
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI2 (+) | DET_INT_HUM_SB9 | Detector Humidity Cable Extension Assemblies | 22 | 6 |  | 12 | V450 | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI10 (-) |  |  | 22 | 19 |  | 12 | V450 | J2 | 19 | CH 13-
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 3 | AI3 (+) | DET_AMB_HUM_H1 | Ambient Humidity Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Humidity Sensor - Humidity Sensor 1
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 3 | AI11 (-) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 4 | AI4 (+) | DET_AMB_HUM_H2 | Ambient Humidity Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Humidity Sensor - Humidity Sensor 2
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 4 | AI12 (-) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0+ | COOL_FLOW_R1_R3 | Coolant Flow Cable Assemblies | 21 | 4 |  | 12 | V450 | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R1-R3)
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0- |  |  | 21 | 17 |  | 12 | V450 | J1 | 17 | CH 3-
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1+ | COOL_FLOW_R4 | Coolant Flow Cable Assemblies | 21 | 5 |  | 12 | V450 | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R4)
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1- |  |  | 21 | 18 |  | 12 | V450 | J1 | 18 | CH 4-
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2+ | COOL_TEMP | Coolant Temperature Cable Assemblies | 21 | 2 |  | 12 | V450 | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2- |  |  | 21 | 15 |  | 12 | V450 | J1 | 15 | CH 1-
Coolant | 17 | N/A | N/A | NI 9239 ADC | 5 | 3 | AI3+ | COOL_LEAK_1 | Coolant Leak Detection - Type 1 - Outputs Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Coolant Leak Signal #1
Coolant | 17 | N/A | N/A | NI 9239 ADC | 5 | 3 | AI3- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 19 |  |  | NI 9485 Relay | 8 | 0 | CH0a | Mpod_CRATE_1_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 1 Enable (+5V for enable)
Mpod Crate Enable | 19 |  |  | NI 9485 Relay | 8 | 0 | CH0b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 20 |  |  | NI 9485 Relay | 8 | 1 | CH1a | Mpod_CRATE_2_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 2 Enable (+5V for enable)
Mpod Crate Enable | 20 |  |  | NI 9485 Relay | 8 | 1 | CH1b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 21 |  |  | NI 9485 Relay | 8 | 2 | CH2a | Mpod_CRATE_3_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 3 Enable (+5V for enable)
Mpod Crate Enable | 21 |  |  | NI 9485 Relay | 8 | 2 | CH2b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 22 |  |  | NI 9485 Relay | 8 | 3 | CH3a | Mpod_CRATE_4_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 4 Enable (+5V for enable)
Mpod Crate Enable | 22 |  |  | NI 9485 Relay | 8 | 3 | CH3b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 23 |  |  | NI 9485 Relay | 8 | 4 | CH4a | Mpod_CRATE_5_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 5 Enable (+5V for enable)
Mpod Crate Enable | 23 |  |  | NI 9485 Relay | 8 | 4 | CH4b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 24 | N/A | N/A | NI 9485 Relay | 8 | 5 | CH5a | CHILLER_ENABLE | Chiller Disable Cable Assembly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 24V for BiRA Power Module via cRio Relay for chiller power
Coolant | 24 | N/A | N/A | NI 9485 Relay | 8 | 5 | CH5b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 25 | N/A | N/A | NI 9485 Relay | 8 | 6 | CH6a | COOL_LEAK_RESET | Coolant Leak Detection - Type 4 - Reset Cable Assembly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Reset for Leak Controller
Coolant | 25 | N/A | N/A | NI 9485 Relay | 8 | 6 | CH6b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## EPICS Slow Control Signals
SVT Slow Control Connections / Signals - By Patch Panel Blocks | [11 empty] | New Signals on 5/20/2015
2015-05-20
Category | SVT Region | SVT Sector/Module | Patch panel Block Type | Patch Panel Block Number | Block Pin # | SC Cable ID | VME Slot # | VME Board Type | Board Serial # | Vme Base Address | Vme Board Configuration | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Signal Name | Comments
HFCB Temp | 1 | 1 | DB25 | 1 | 1 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | DB25 | 1 | 14 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 1 | 1 | DB25 | 1 | 2 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R1S1B_Slot2 | SVT - HFCB Temp R1 M1 Bottom
HFCB Temp | 1 | 1 | DB25 | 1 | 15 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 1 | 2 | DB25 | 1 | 3 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R1S2T_Slot2 | SVT - HFCB Temp R1 M2 Top
HFCB Temp | 1 | 2 | DB25 | 1 | 16 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 1 | 2 | DB25 | 1 | 4 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R1S2B_Slot2 | SVT - HFCB Temp R1 M2 Bottom
HFCB Temp | 1 | 2 | DB25 | 1 | 17 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 1 | 3 | DB25 | 1 | 5 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R1S3T_Slot2 | SVT - HFCB Temp R1 M3 Top
HFCB Temp | 1 | 3 | DB25 | 1 | 18 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 1 | 3 | DB25 | 1 | 6 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R1S3B_Slot2 | SVT - HFCB Temp R1 M3 Bottom
HFCB Temp | 1 | 3 | DB25 | 1 | 19 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 1 | 4 | DB25 | 1 | 7 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R1S4T_Slot2 | SVT - HFCB Temp R1 M4 Top
HFCB Temp | 1 | 4 | DB25 | 1 | 20 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 1 | 4 | DB25 | 1 | 8 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R1S4B_Slot2 | SVT - HFCB Temp R1 M4 Bottom
HFCB Temp | 1 | 4 | DB25 | 1 | 21 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 1 | 9 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB1_T1_SL2 | Detector Environmental Temperature Sensor Board 1 - Temp Sensor 1
RTD Temp |  |  | DB25 | 1 | 22 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 1 | 10 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 1 | 23 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 1 | 11 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB1_T2_SL2 | Detector Environmental Temperature Sensor Board 1 - Temp Sensor 2
RTD Temp |  |  | DB25 | 1 | 24 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 1 | 12 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 1 | 25 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 1 | 5 | DB25 | 2 | 1 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R1S5T_Slot2 | SVT - HFCB Temp R1 M5 Top
HFCB Temp | 1 | 5 | DB25 | 2 | 14 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 1 | 5 | DB25 | 2 | 2 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R1S5B_Slot2 | SVT - HFCB Temp R1 M5 Bottom
HFCB Temp | 1 | 5 | DB25 | 2 | 15 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 1 | 6 | DB25 | 2 | 3 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R1S6T_Slot2 | SVT - HFCB Temp R1 M6 Top
HFCB Temp | 1 | 6 | DB25 | 2 | 16 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 1 | 6 | DB25 | 2 | 4 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R1S6B_Slot2 | SVT - HFCB Temp R1 M6 Bottom
HFCB Temp | 1 | 6 | DB25 | 2 | 17 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 1 | 7 | DB25 | 2 | 5 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R1S7T_Slot2 | SVT - HFCB Temp R1 M7 Top
HFCB Temp | 1 | 7 | DB25 | 2 | 18 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 1 | 7 | DB25 | 2 | 6 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R1S7B_Slot2 | SVT - HFCB Temp R1 M7 Bottom
HFCB Temp | 1 | 7 | DB25 | 2 | 19 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 1 | 8 | DB25 | 2 | 7 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R1S8T_Slot2 | SVT - HFCB Temp R1 M8 Top
HFCB Temp | 1 | 8 | DB25 | 2 | 20 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 1 | 8 | DB25 | 2 | 8 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R1S8B_Slot2 | SVT - HFCB Temp R1 M8 Bottom
HFCB Temp | 1 | 8 | DB25 | 2 | 21 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 2 | 9 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB2_T1_SL2 | Detector Environmental Temperature Sensor Board 2 - Temp Sensor 1
RTD Temp |  |  | DB25 | 2 | 22 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 2 | 10 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 2 | 23 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 2 | 11 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB2_T2_SL2 | Detector Environmental Temperature Sensor Board 2 - Temp Sensor 2
RTD Temp |  |  | DB25 | 2 | 24 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 2 | 12 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 2 | 25 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 1 | 9 | DB25 | 3 | 1 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S9T_Slot3 | SVT - HFCB Temp R1 M9 Top
HFCB Temp | 1 | 9 | DB25 | 3 | 14 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 1 | 9 | DB25 | 3 | 2 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R1S9B_Slot3 | SVT - HFCB Temp R1 M9 Bottom
HFCB Temp | 1 | 9 | DB25 | 3 | 15 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 1 | 10 | DB25 | 3 | 3 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R1S10T_Slot3 | SVT - HFCB Temp R1 M10 Top
HFCB Temp | 1 | 10 | DB25 | 3 | 16 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 1 | 10 | DB25 | 3 | 4 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R1S10B_Slot3 | SVT - HFCB Temp R1 M10 Bottom
HFCB Temp | 1 | 10 | DB25 | 3 | 17 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 2 | 1 | DB25 | 3 | 5 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 1 | DB25 | 3 | 18 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 2 | 1 | DB25 | 3 | 6 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R2S1B_Slot3 | SVT - HFCB Temp R2 M1 Bottom
HFCB Temp | 2 | 1 | DB25 | 3 | 19 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 2 | 2 | DB25 | 3 | 7 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R2S2T_Slot3 | SVT - HFCB Temp R2 M2 Top
HFCB Temp | 2 | 2 | DB25 | 3 | 20 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 2 | 2 | DB25 | 3 | 8 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R2S2B_Slot3 | SVT - HFCB Temp R2 M2 Bottom
HFCB Temp | 2 | 2 | DB25 | 3 | 21 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 3 | 9 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB3_T1 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 1
RTD Temp |  |  | DB25 | 3 | 22 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 3 | 10 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 3 | 23 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 3 | 11 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp |  |  | DB25 | 3 | 24 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 3 | 12 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 3 | 25 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 2 | 3 | DB25 | 4 | 1 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R2S3T_Slot3 | SVT - HFCB Temp R2 M3 Top
HFCB Temp | 2 | 3 | DB25 | 4 | 14 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 2 | 3 | DB25 | 4 | 2 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R2S3B_Slot3 | SVT - HFCB Temp R2 M3 Bottom
HFCB Temp | 2 | 3 | DB25 | 4 | 15 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 2 | 4 | DB25 | 4 | 3 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R2S4T_Slot3 | SVT - HFCB Temp R2 M4 Top
HFCB Temp | 2 | 4 | DB25 | 4 | 16 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 2 | 4 | DB25 | 4 | 4 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R2S4B_Slot3 | SVT - HFCB Temp R2 M4 Bottom
HFCB Temp | 2 | 4 | DB25 | 4 | 17 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 2 | 5 | DB25 | 4 | 5 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R2S5T_Slot3 | SVT - HFCB Temp R2 M5 Top
HFCB Temp | 2 | 5 | DB25 | 4 | 18 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 2 | 5 | DB25 | 4 | 6 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R2S5B_Slot3 | SVT - HFCB Temp R2 M5 Bottom
HFCB Temp | 2 | 5 | DB25 | 4 | 19 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 2 | 6 | DB25 | 4 | 7 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R2S6T_Slot3 | SVT - HFCB Temp R2 M6 Top
HFCB Temp | 2 | 6 | DB25 | 4 | 20 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 2 | 6 | DB25 | 4 | 8 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R2S6B_Slot3 | SVT - HFCB Temp R2 M6 Bottom
HFCB Temp | 2 | 6 | DB25 | 4 | 21 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 4 | 9 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB4_T1_SL3 | Detector Environmental Temperature Sensor Board 4 - Temp Sensor 1
RTD Temp |  |  | DB25 | 4 | 22 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 4 | 10 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 4 | 23 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 4 | 11 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB4_T2_SL3 | Detector Environmental Temperature Sensor Board 4 - Temp Sensor 2
RTD Temp |  |  | DB25 | 4 | 24 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 4 | 12 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 4 | 25 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 2 | 7 | DB25 | 5 | 1 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R2S7T_Slot4 | SVT - HFCB Temp R2 M7 Top
HFCB Temp | 2 | 7 | DB25 | 5 | 14 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 2 | 7 | DB25 | 5 | 2 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R2S7B_Slot4 | SVT - HFCB Temp R2 M7 Bottom
HFCB Temp | 2 | 7 | DB25 | 5 | 15 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 2 | 8 | DB25 | 5 | 3 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R2S8T_Slot4 | SVT - HFCB Temp R2 M8 Top
HFCB Temp | 2 | 8 | DB25 | 5 | 16 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 2 | 8 | DB25 | 5 | 4 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R2S8B_Slot4 | SVT - HFCB Temp R2 M8 Bottom
HFCB Temp | 2 | 8 | DB25 | 5 | 17 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 2 | 9 | DB25 | 5 | 5 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S9T_Slot4 | SVT - HFCB Temp R2 M9 Top
HFCB Temp | 2 | 9 | DB25 | 5 | 18 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 2 | 9 | DB25 | 5 | 6 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R2S9B_Slot4 | SVT - HFCB Temp R2 M9 Bottom
HFCB Temp | 2 | 9 | DB25 | 5 | 19 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 2 | 10 | DB25 | 5 | 7 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R2S10T_Slot4 | SVT - HFCB Temp R2 M10 Top
HFCB Temp | 2 | 10 | DB25 | 5 | 20 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 2 | 10 | DB25 | 5 | 8 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R2S10B_Slot4 | SVT - HFCB Temp R2 M10 Bottom
HFCB Temp | 2 | 10 | DB25 | 5 | 21 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 5 | 9 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB5_T1_SL4 | Detector Environmental Temperature Sensor Board 5 - Temp Sensor 1
RTD Temp |  |  | DB25 | 5 | 22 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 5 | 10 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 5 | 23 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 5 | 11 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB5_T2_SL4 | Detector Environmental Temperature Sensor Board 5 - Temp Sensor 2
RTD Temp |  |  | DB25 | 5 | 24 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 5 | 12 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 5 | 25 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 2 | 11 | DB25 | 6 | 1 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R2S11T_Slot4 | SVT - HFCB Temp R2 M11 Top
HFCB Temp | 2 | 11 | DB25 | 6 | 14 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 2 | 11 | DB25 | 6 | 2 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R2S11B_Slot4 | SVT - HFCB Temp R2 M11 Bottom
HFCB Temp | 2 | 11 | DB25 | 6 | 15 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 2 | 12 | DB25 | 6 | 3 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R2S12T_Slot4 | SVT - HFCB Temp R2 M12 Top
HFCB Temp | 2 | 12 | DB25 | 6 | 16 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 2 | 12 | DB25 | 6 | 4 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R2S12B_Slot4 | SVT - HFCB Temp R2 M12 Bottom
HFCB Temp | 2 | 12 | DB25 | 6 | 17 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 2 | 13 | DB25 | 6 | 5 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R2S13T_Slot4 | SVT - HFCB Temp R2 M13 Top
HFCB Temp | 2 | 13 | DB25 | 6 | 18 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 2 | 13 | DB25 | 6 | 6 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R2S13B_Slot4 | SVT - HFCB Temp R2 M13 Bottom
HFCB Temp | 2 | 13 | DB25 | 6 | 19 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 2 | 14 | DB25 | 6 | 7 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R2S14T_Slot4 | SVT - HFCB Temp R2 M14 Top
HFCB Temp | 2 | 14 | DB25 | 6 | 20 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 2 | 14 | DB25 | 6 | 8 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R2S14B_Slot4 | SVT - HFCB Temp R2 M14 Bottom
HFCB Temp | 2 | 14 | DB25 | 6 | 21 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 6 | 9 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB6_T1_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 1
RTD Temp |  |  | DB25 | 6 | 22 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 6 | 10 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 6 | 23 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 6 | 11 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp |  |  | DB25 | 6 | 24 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 6 | 12 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 6 | 25 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 1 | DB25 | 7 | 1 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 1 | DB25 | 7 | 14 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 1 | DB25 | 7 | 2 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S1B_Slot5 | SVT - HFCB Temp R3 M1 Bottom
HFCB Temp | 3 | 1 | DB25 | 7 | 15 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 2 | DB25 | 7 | 3 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S2T_Slot5 | SVT - HFCB Temp R3 M2 Top
HFCB Temp | 3 | 2 | DB25 | 7 | 16 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 2 | DB25 | 7 | 4 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S2B_Slot5 | SVT - HFCB Temp R3 M2 Bottom
HFCB Temp | 3 | 2 | DB25 | 7 | 17 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 3 | 3 | DB25 | 7 | 5 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R3S3T_Slot5 | SVT - HFCB Temp R3 M3 Top
HFCB Temp | 3 | 3 | DB25 | 7 | 18 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | DB25 | 7 | 6 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R3S3B_Slot5 | SVT - HFCB Temp R3 M3 Bottom
HFCB Temp | 3 | 3 | DB25 | 7 | 19 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 3 | 4 | DB25 | 7 | 7 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R3S4T_Slot5 | SVT - HFCB Temp R3 M4 Top
HFCB Temp | 3 | 4 | DB25 | 7 | 20 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 3 | 4 | DB25 | 7 | 8 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R3S4B_Slot5 | SVT - HFCB Temp R3 M4 Bottom
HFCB Temp | 3 | 4 | DB25 | 7 | 21 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp | 4 |  | DB25 | 7 | 9 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB7_T1_SL5 | Detector Environmental Temperature Sensor Board 7- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 7 | 22 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp | 4 |  | DB25 | 7 | 10 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp | 4 |  | DB25 | 7 | 23 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp | 4 |  | DB25 | 7 | 11 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB7_T2_SL5 | Detector Environmental Temperature Sensor Board 7- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 7 | 24 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp | 4 |  | DB25 | 7 | 12 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp | 4 |  | DB25 | 7 | 25 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 3 | 5 | DB25 | 8 | 1 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R3S5T_Slot5 | SVT - HFCB Temp R3 M5 Top
HFCB Temp | 3 | 5 | DB25 | 8 | 14 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 3 | 5 | DB25 | 8 | 2 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R3S5B_Slot5 | SVT - HFCB Temp R3 M5 Bottom
HFCB Temp | 3 | 5 | DB25 | 8 | 15 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 3 | 6 | DB25 | 8 | 3 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R3S6T_Slot5 | SVT - HFCB Temp R3 M6 Top
HFCB Temp | 3 | 6 | DB25 | 8 | 16 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 3 | 6 | DB25 | 8 | 4 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R3S6B_Slot5 | SVT - HFCB Temp R3 M6 Bottom
HFCB Temp | 3 | 6 | DB25 | 8 | 17 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 3 | 7 | DB25 | 8 | 5 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R3S7T_Slot5 | SVT - HFCB Temp R3 M7 Top
HFCB Temp | 3 | 7 | DB25 | 8 | 18 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 3 | 7 | DB25 | 8 | 6 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R3S7B_Slot5 | SVT - HFCB Temp R3 M7 Bottom
HFCB Temp | 3 | 7 | DB25 | 8 | 19 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 3 | 8 | DB25 | 8 | 7 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R3S8T_Slot5 | SVT - HFCB Temp R3 M8 Top
HFCB Temp | 3 | 8 | DB25 | 8 | 20 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 3 | 8 | DB25 | 8 | 8 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R3S8B_Slot5 | SVT - HFCB Temp R3 M8 Bottom
HFCB Temp | 3 | 8 | DB25 | 8 | 21 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp | 4 |  | DB25 | 8 | 9 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB8_T1_SL5 | Detector Environmental Temperature Sensor Board 8- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 8 | 22 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp | 4 |  | DB25 | 8 | 10 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp | 4 |  | DB25 | 8 | 23 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp | 4 |  | DB25 | 8 | 11 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB8_T2_SL5 | Detector Environmental Temperature Sensor Board 8- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 8 | 24 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp | 4 |  | DB25 | 8 | 12 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp | 4 |  | DB25 | 8 | 25 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 9 | DB25 | 9 | 1 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S9T_Slot6 | SVT - HFCB Temp R3 M9 Top
HFCB Temp | 3 | 9 | DB25 | 9 | 14 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 9 | DB25 | 9 | 2 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S9B_Slot6 | SVT - HFCB Temp R3 M9 Bottom
HFCB Temp | 3 | 9 | DB25 | 9 | 15 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 10 | DB25 | 9 | 3 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S10T_Slot6 | SVT - HFCB Temp R3 M10 Top
HFCB Temp | 3 | 10 | DB25 | 9 | 16 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 10 | DB25 | 9 | 4 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S10B_Slot6 | SVT - HFCB Temp R3 M10 Bottom
HFCB Temp | 3 | 10 | DB25 | 9 | 17 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 3 | 11 | DB25 | 9 | 5 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R3S11T_Slot6 | SVT - HFCB Temp R3 M11 Top
HFCB Temp | 3 | 11 | DB25 | 9 | 18 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 3 | 11 | DB25 | 9 | 6 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R3S11B_Slot6 | SVT - HFCB Temp R3 M11 Bottom
HFCB Temp | 3 | 11 | DB25 | 9 | 19 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 3 | 12 | DB25 | 9 | 7 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R3S12T_Slot6 | SVT - HFCB Temp R3 M12 Top
HFCB Temp | 3 | 12 | DB25 | 9 | 20 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 3 | 12 | DB25 | 9 | 8 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R3S12B_Slot6 | SVT - HFCB Temp R3 M12 Bottom
HFCB Temp | 3 | 12 | DB25 | 9 | 21 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp | 4 |  | DB25 | 9 | 9 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB9_T1_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 9 | 22 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp | 4 |  | DB25 | 9 | 10 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp | 4 |  | DB25 | 9 | 23 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp | 4 |  | DB25 | 9 | 11 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 9 | 24 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp | 4 |  | DB25 | 9 | 12 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp | 4 |  | DB25 | 9 | 25 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 3 | 13 | DB25 | 10 | 1 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R3S13T_Slot6 | SVT - HFCB Temp R3 M13 Top
HFCB Temp | 3 | 13 | DB25 | 10 | 14 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 3 | 13 | DB25 | 10 | 2 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R3S13B_Slot6 | SVT - HFCB Temp R3 M13 Bottom
HFCB Temp | 3 | 13 | DB25 | 10 | 15 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 3 | 14 | DB25 | 10 | 3 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R3S14T_Slot6 | SVT - HFCB Temp R3 M14 Top
HFCB Temp | 3 | 14 | DB25 | 10 | 16 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 3 | 14 | DB25 | 10 | 4 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R3S14B_Slot6 | SVT - HFCB Temp R3 M14 Bottom
HFCB Temp | 3 | 14 | DB25 | 10 | 17 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 3 | 15 | DB25 | 10 | 5 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R3S15T_Slot6 | SVT - HFCB Temp R3 M15 Top
HFCB Temp | 3 | 15 | DB25 | 10 | 18 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 3 | 15 | DB25 | 10 | 6 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R3S15B_Slot6 | SVT - HFCB Temp R3 M15 Bottom
HFCB Temp | 3 | 15 | DB25 | 10 | 19 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 3 | 16 | DB25 | 10 | 7 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R3S16T_Slot6 | SVT - HFCB Temp R3 M16 Top
HFCB Temp | 3 | 16 | DB25 | 10 | 20 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 3 | 16 | DB25 | 10 | 8 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R3S16B_Slot6 | SVT - HFCB Temp R3 M16 Bottom
HFCB Temp | 3 | 16 | DB25 | 10 | 21 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp | 4 |  | DB25 | 10 | 9 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB10_T1_SL6 | Detector Environmental Temperature Sensor Board 10- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 10 | 22 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp | 4 |  | DB25 | 10 | 10 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp | 4 |  | DB25 | 10 | 23 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp | 4 |  | DB25 | 10 | 11 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB10_T2_SL6 | Detector Environmental Temperature Sensor Board 10- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 10 | 24 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp | 4 |  | DB25 | 10 | 12 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp | 4 |  | DB25 | 10 | 25 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 17 | DB25 | 11 | 1 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S17T_Slot7 | SVT - HFCB Temp R3 M17 Top
HFCB Temp | 3 | 17 | DB25 | 11 | 14 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 17 | DB25 | 11 | 2 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S17B_Slot7 | SVT - HFCB Temp R3 M17 Bottom
HFCB Temp | 3 | 17 | DB25 | 11 | 15 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 18 | DB25 | 11 | 3 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S18T_Slot7 | SVT - HFCB Temp R3 M18 Top
HFCB Temp | 3 | 18 | DB25 | 11 | 16 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 18 | DB25 | 11 | 4 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S18B_Slot7 | SVT - HFCB Temp R3 M18 Bottom
HFCB Temp | 3 | 18 | DB25 | 11 | 17 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
|  |  | DB25 | 11 | 5 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+
|  |  | DB25 | 11 | 18 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
|  |  | DB25 | 11 | 6 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+
|  |  | DB25 | 11 | 19 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
|  |  | DB25 | 11 | 7 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+
|  |  | DB25 | 11 | 20 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
|  |  | DB25 | 11 | 8 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+
|  |  |  | 11 | 21 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 11 | 9 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 11 | 22 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 11 | 10 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 11 | 23 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 11 | 11 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 11 | 24 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 11 | 12 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 11 | 25 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
|  |  | DB25 | 12 | 1 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+
|  |  | DB25 | 12 | 14 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
|  |  | DB25 | 12 | 2 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+
|  |  | DB25 | 12 | 15 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
|  |  | DB25 | 12 | 3 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+
|  |  | DB25 | 12 | 16 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
|  |  | DB25 | 12 | 4 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+
|  |  | DB25 | 12 | 17 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
|  |  | DB25 | 12 | 5 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+
|  |  | DB25 | 12 | 18 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
|  |  | DB25 | 12 | 6 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+
|  |  | DB25 | 12 | 19 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
|  |  | DB25 | 12 | 7 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+
|  |  | DB25 | 12 | 20 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
|  |  | DB25 | 12 | 8 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+
|  |  | DB25 | 12 | 21 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 12 | 9 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 12 | 22 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 12 | 10 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 12 | 23 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 12 | 11 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 12 | 24 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 12 | 12 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 12 | 25 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 4 | 1 | DB25 | 13 | 1 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 1 | DB25 | 13 | 14 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 1 | DB25 | 13 | 2 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S1B_Slot8 | SVT - HFCB Temp R4 M1 Bottom
HFCB Temp | 4 | 1 | DB25 | 13 | 15 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 2 | DB25 | 13 | 3 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S2T_Slot8 | SVT - HFCB Temp R4 M2 Top
HFCB Temp | 4 | 2 | DB25 | 13 | 16 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 2 | DB25 | 13 | 4 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S2B_Slot8 | SVT - HFCB Temp R4 M2 Bottom
HFCB Temp | 4 | 2 | DB25 | 13 | 17 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 3 | DB25 | 13 | 5 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S3T_Slot8 | SVT - HFCB Temp R4 M3 Top
HFCB Temp | 4 | 3 | DB25 | 13 | 18 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 3 | DB25 | 13 | 6 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S3B_Slot8 | SVT - HFCB Temp R4 M3 Bottom
HFCB Temp | 4 | 3 | DB25 | 13 | 19 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 4 | DB25 | 13 | 7 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S4T_Slot8 | SVT - HFCB Temp R4 M4 Top
HFCB Temp | 4 | 4 | DB25 | 13 | 20 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 4 | DB25 | 13 | 8 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S4B_Slot8 | SVT - HFCB Temp R4 M4 Bottom
HFCB Temp | 4 | 4 | DB25 | 13 | 21 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 13 | 9 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 13 | 22 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 13 | 10 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 13 | 23 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 13 | 11 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 13 | 24 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 13 | 12 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 13 | 25 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 5 | DB25 | 14 | 1 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S5T_Slot8 | SVT - HFCB Temp R4 M5 Top
HFCB Temp | 4 | 5 | DB25 | 14 | 14 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 5 | DB25 | 14 | 2 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S5B_Slot8 | SVT - HFCB Temp R4 M5 Bottom
HFCB Temp | 4 | 5 | DB25 | 14 | 15 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 6 | DB25 | 14 | 3 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S6T_Slot8 | SVT - HFCB Temp R4 M6 Top
HFCB Temp | 4 | 6 | DB25 | 14 | 16 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 6 | DB25 | 14 | 4 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S6B_Slot8 | SVT - HFCB Temp R4 M6 Bottom
HFCB Temp | 4 | 6 | DB25 | 14 | 17 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 7 | DB25 | 14 | 5 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S7T_Slot8 | SVT - HFCB Temp R4 M7 Top
HFCB Temp | 4 | 7 | DB25 | 14 | 18 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 7 | DB25 | 14 | 6 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S7B_Slot8 | SVT - HFCB Temp R4 M7 Bottom
HFCB Temp | 4 | 7 | DB25 | 14 | 19 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 8 | DB25 | 14 | 7 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S8T_Slot8 | SVT - HFCB Temp R4 M8 Top
HFCB Temp | 4 | 8 | DB25 | 14 | 20 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 8 | DB25 | 14 | 8 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S8B_Slot8 | SVT - HFCB Temp R4 M8 Bottom
HFCB Temp | 4 | 8 | DB25 | 14 | 21 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 14 | 9 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 14 | 22 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 14 | 10 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 14 | 23 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 14 | 11 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 14 | 24 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 14 | 12 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 14 | 25 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdB S-
HFCB Temp | 4 | 9 | DB25 | 15 | 1 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S9T_Slot9 | SVT - HFCB Temp R4 M9 Top
HFCB Temp | 4 | 9 | DB25 | 15 | 14 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 9 | DB25 | 15 | 2 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S9B_Slot9 | SVT - HFCB Temp R4 M9 Bottom
HFCB Temp | 4 | 9 | DB25 | 15 | 15 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 10 | DB25 | 15 | 3 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S10T_Slot9 | SVT - HFCB Temp R4 M10 Top
HFCB Temp | 4 | 10 | DB25 | 15 | 16 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 10 | DB25 | 15 | 4 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S10B_Slot9 | SVT - HFCB Temp R4 M10 Bottom
HFCB Temp | 4 | 10 | DB25 | 15 | 17 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 11 | DB25 | 15 | 5 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S11T_Slot9 | SVT - HFCB Temp R4 M11 Top
HFCB Temp | 4 | 11 | DB25 | 15 | 18 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 11 | DB25 | 15 | 6 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S11B_Slot9 | SVT - HFCB Temp R4 M11 Bottom
HFCB Temp | 4 | 11 | DB25 | 15 | 19 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 12 | DB25 | 15 | 7 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S12T_Slot9 | SVT - HFCB Temp R4 M12 Top
HFCB Temp | 4 | 12 | DB25 | 15 | 20 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 12 | DB25 | 15 | 8 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S12B_Slot9 | SVT - HFCB Temp R4 M12 Bottom
HFCB Temp | 4 | 12 | DB25 | 15 | 21 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 15 | 9 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 15 | 22 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 15 | 10 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 15 | 23 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 15 | 11 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 15 | 24 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 15 | 12 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 15 | 25 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 13 | DB25 | 16 | 1 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S13T_Slot9 | SVT - HFCB Temp R4 M13 Top
HFCB Temp | 4 | 13 | DB25 | 16 | 14 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 13 | DB25 | 16 | 2 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S13B_Slot9 | SVT - HFCB Temp R4 M13 Bottom
HFCB Temp | 4 | 13 | DB25 | 16 | 15 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 14 | DB25 | 16 | 3 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S14T_Slot9 | SVT - HFCB Temp R4 M14 Top
HFCB Temp | 4 | 14 | DB25 | 16 | 16 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 14 | DB25 | 16 | 4 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S14B_Slot9 | SVT - HFCB Temp R4 M14 Bottom
HFCB Temp | 4 | 14 | DB25 | 16 | 17 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 15 | DB25 | 16 | 5 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S15T_Slot9 | SVT - HFCB Temp R4 M15 Top
HFCB Temp | 4 | 15 | DB25 | 16 | 18 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 15 | DB25 | 16 | 6 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S15B_Slot9 | SVT - HFCB Temp R4 M15 Bottom
HFCB Temp | 4 | 15 | DB25 | 16 | 19 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 16 | DB25 | 16 | 7 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S16T_Slot9 | SVT - HFCB Temp R4 M16 Top
HFCB Temp | 4 | 16 | DB25 | 16 | 20 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 16 | DB25 | 16 | 8 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S16B_Slot9 | SVT - HFCB Temp R4 M16 Bottom
HFCB Temp | 4 | 16 | DB25 | 16 | 21 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 16 | 9 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 16 | 22 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 16 | 10 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 16 | 23 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 16 | 11 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 16 | 24 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 16 | 12 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 16 | 25 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdB S-
HFCB Temp | 4 | 17 | DB25 | 17 | 1 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S17T_Slot10 | SVT - HFCB Temp R4 M17 Top
HFCB Temp | 4 | 17 | DB25 | 17 | 14 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 17 | DB25 | 17 | 2 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S17B_Slot10 | SVT - HFCB Temp R4 M17 Bottom
HFCB Temp | 4 | 17 | DB25 | 17 | 15 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 18 | DB25 | 17 | 3 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S18T_Slot10 | SVT - HFCB Temp R4 M18 Top
HFCB Temp | 4 | 18 | DB25 | 17 | 16 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 18 | DB25 | 17 | 4 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S18B_Slot10 | SVT - HFCB Temp R4 M18 Bottom
HFCB Temp | 4 | 18 | DB25 | 17 | 17 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 19 | DB25 | 17 | 5 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S19T_Slot10 | SVT - HFCB Temp R4 M19 Top
HFCB Temp | 4 | 19 | DB25 | 17 | 18 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 19 | DB25 | 17 | 6 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S19B_Slot10 | SVT - HFCB Temp R4 M19 Bottom
HFCB Temp | 4 | 19 | DB25 | 17 | 19 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 20 | DB25 | 17 | 7 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S20T_Slot10 | SVT - HFCB Temp R4 M20 Top
HFCB Temp | 4 | 20 | DB25 | 17 | 20 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 20 | DB25 | 17 | 8 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S20B_Slot10 | SVT - HFCB Temp R4 M20 Bottom
HFCB Temp | 4 | 20 | DB25 | 17 | 21 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 17 | 9 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 17 | 22 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 17 | 10 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 17 | 23 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 17 | 11 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 17 | 24 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 17 | 12 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 17 | 25 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 21 | DB25 | 18 | 1 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S21T_Slot10 | SVT - HFCB Temp R4 M21 Top
HFCB Temp | 4 | 21 | DB25 | 18 | 14 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 21 | DB25 | 18 | 2 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S21B_Slot10 | SVT - HFCB Temp R4 M21 Bottom
HFCB Temp | 4 | 21 | DB25 | 18 | 15 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 22 | DB25 | 18 | 3 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S22T_Slot10 | SVT - HFCB Temp R4 M22 Top
HFCB Temp | 4 | 22 | DB25 | 18 | 16 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 22 | DB25 | 18 | 4 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S22B_Slot10 | SVT - HFCB Temp R4 M22 Bottom
HFCB Temp | 4 | 22 | DB25 | 18 | 17 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 23 | DB25 | 18 | 5 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S23T_Slot10 | SVT - HFCB Temp R4 M23 Top
HFCB Temp | 4 | 23 | DB25 | 18 | 18 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 23 | DB25 | 18 | 6 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S23B_Slot10 | SVT - HFCB Temp R4 M23 Bottom
HFCB Temp | 4 | 23 | DB25 | 18 | 19 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 24 | DB25 | 18 | 7 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S24T_Slot10 | SVT - HFCB Temp R4 M24 Top
HFCB Temp | 4 | 24 | DB25 | 18 | 20 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 24 | DB25 | 18 | 8 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S24B_Slot10 | SVT - HFCB Temp R4 M24 Bottom
HFCB Temp | 4 | 24 | DB25 | 18 | 21 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 18 | 9 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 18 | 22 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 18 | 10 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 18 | 23 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 18 | 11 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 18 | 24 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 18 | 12 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 18 | 25 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
Humidity Sensor |  |  | DB25 | 19 | 1 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_ENV_Hum_SB1_H1_SL11 | Detector Environmental Humidity Sensor Board 1 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 14 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
Humidity Sensor |  |  | DB25 | 19 | 2 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_ENV_Hum_SB1_H2_SL11 | Detector Environmental Humidity Sensor Board 1 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 15 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
Humidity Sensor |  |  | DB25 | 19 | 3 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_ENV_Hum_SB2_H1_SL11 | Detector Environmental Humidity Sensor Board 2 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 16 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
Humidity Sensor |  |  | DB25 | 19 | 4 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_ENV_Hum_SB2_H2_SL11 | Detector Environmental Humidity Sensor Board 2 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 17 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
Humidity Sensor |  |  | DB25 | 19 | 5 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_ENV_Hum_SB3_H1_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 18 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
Humidity Sensor |  |  | DB25 | 19 | 6 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 19 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
Humidity Sensor |  |  | DB25 | 19 | 7 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_ENV_Hum_SB4_H1_SL11 | Detector Environmental Humidity Sensor Board 4 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 20 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
Humidity Sensor |  |  | DB25 | 19 | 8 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_ENV_Hum_SB4_H2_SL11 | Detector Environmental Humidity Sensor Board 4 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 21 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 19 | 9 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_EX_ENV_TEMP_SB1_T1_SL11 | External Environmental Temperature Sensor Board 1- Temp Sensor 1
RTD Temp |  |  | DB25 | 19 | 22 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 19 | 10 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 19 | 23 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 19 | 11 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_EX_ENV_TEMP_SB1_T2_SL11 | External Environmental Temperature Sensor Board 1- Temp Sensor 2
RTD Temp |  |  | DB25 | 19 | 24 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 19 | 12 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 19 | 25 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
Humidity Sensor |  |  | DB25 | 20 | 1 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_ENV_Hum_SB5_H1_SL11 | Detector Environmental Humidity Sensor Board 5 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 14 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
Humidity Sensor |  |  | DB25 | 20 | 2 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_ENV_Hum_SB5_H2_SL11 | Detector Environmental Humidity Sensor Board 5 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 15 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
Humidity Sensor |  |  | DB25 | 20 | 3 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_ENV_Hum_SB6_H1_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 16 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
Humidity Sensor |  |  | DB25 | 20 | 4 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 17 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
Humidity Sensor |  |  | DB25 | 20 | 5 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_EX_ENV_Hum_SB1_H1_SL11 | External Environmental Humidity Sensor Board 1 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 18 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
Humidity Sensor |  |  | DB25 | 20 | 6 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_EX_ENV_Hum_SB1_H2_SL11 | External Environmental Humidity Sensor Board 1 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 19 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
Humidity Sensor |  |  | DB25 | 20 | 7 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_EX_ENV_Hum_SB2_H1_SL11 | External Environmental Humidity Sensor Board 2 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 20 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
Humidity Sensor |  |  | DB25 | 20 | 8 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_EX_ENV_Hum_SB2_H2_SL11 | External Environmental Humidity Sensor Board 2 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 21 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 20 | 9 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_EX_ENV_TEMP_SB2_T1_SL11 | External Environmental Temperature Sensor Board 2- Temp Sensor 1
RTD Temp |  |  | DB25 | 20 | 22 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 20 | 10 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 20 | 23 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 20 | 11 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_EX_ENV_TEMP_SB2_T2_SL11 | External Environmental Temperature Sensor Board 2- Temp Sensor 2
RTD Temp |  |  | DB25 | 20 | 24 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 20 | 12 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 20 | 25 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
Coolant |  |  | DB25 | 21 | 1 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_Cool_Inlet_Flow | Inlet Coolant Flow Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 14 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
Coolant |  |  | DB25 | 21 | 2 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 15 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
Coolant |  |  | DB25 | 21 | 3 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_Cool_Inlet_Pres | Inlet Coolant Pressure Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 16 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
Coolant |  |  | DB25 | 21 | 4 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter
Coolant |  |  | DB25 | 21 | 17 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
|  |  | DB25 | 21 | 5 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter
|  |  | DB25 | 21 | 18 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
|  |  | DB25 | 21 | 6 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+
|  |  | DB25 | 21 | 19 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
|  |  | DB25 | 21 | 7 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+
|  |  | DB25 | 21 | 20 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
|  |  | DB25 | 21 | 8 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+
|  |  | DB25 | 21 | 21 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 21 | 9 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 21 | 22 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 21 | 10 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 21 | 23 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 21 | 11 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 21 | 24 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 21 | 12 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 21 | 25 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
Humidity Sensor | 4 |  | DB25 | 22 | 1 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_ENV_Hum_SB7_H1_SL12 | Detector Environmental Humidity Sensor Board 7 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 14 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
Humidity Sensor | 4 |  | DB25 | 22 | 2 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_ENV_Hum_SB7_H2_SL12 | Detector Environmental Humidity Sensor Board 7 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 15 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
Humidity Sensor | 4 |  | DB25 | 22 | 3 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_ENV_Hum_SB8_H1_SL12 | Detector Environmental Humidity Sensor Board 8- Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 16 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
Humidity Sensor | 4 |  | DB25 | 22 | 4 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB8_H2_SL12 | Detector Environmental Humidity Sensor Board 8 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 17 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
Humidity Sensor | 4 |  | DB25 | 22 | 5 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_ENV_Hum_SB9_H1_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 18 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
Humidity Sensor | 4 |  | DB25 | 22 | 6 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 19 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
Humidity Sensor | 4 |  | DB25 | 22 | 7 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_ENV_Hum_SB10_H1_SL12 | Detector Environmental Humidity Sensor Board 10 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 20 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
Humidity Sensor | 4 |  | DB25 | 22 | 8 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_ENV_Hum_SB10_H2_SL12 | Detector Environmental Humidity Sensor Board 10 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 21 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 22 | 9 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 22 | 22 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 22 | 10 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 22 | 23 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 22 | 11 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 22 | 24 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 22 | 12 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 22 | 25 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-

## Parts
SVT Hardware Interlock System Components / Orders
Item | Manufacturer | Manufacturer Part# | Company | Company Part # | Description | Qty. | Unit Price | Total Cost | PR | PO | Received? | PRB Item #
Ferrule | Altech Corp | 2400.0 | Allied Elec. | 70078405 | 16 AWG (100 pk.) | 5 | 9.55 | 47.75 | PR 354904P | 12A2609008-708 | YES | 13
Ferrule | Altech Corp | 2622.0 | Allied Elec. | 70078400 | 22AWG (100 pk.) | 5 | 7.96 | 39.8 | PR 354904P | 12A2609008-708 | Yes | 14
Ferrule | Altech Corp | 2399.0 | Allied Elec. | 70078404 | 18 AWG (100 pk.) | 5 | 7.96 | 39.8 | PR 354904P | 12A2609008-708 | Yes | 15
Ferrule | Altech Corp | 2621.0 | Allied Elec. | 70078399 | 24AWG (100 pk.) | 5 | 7.96 | 39.8 | PR 354904P | 12A2609008-708 | Yes | 16
Control Cable | Alpha Wire | 1218C SL005 | Newark | 85K9585 | 8 Conductor; 24 AWG; Shielded, 100' | 2 | 183.11 | 366.22 | PR 354904P | 12A2609008-708 | Yes | 19
DB9 Male Connectors | TE CONNECTIVITY / AMP | 5-747904-2 | Newark | 52K3762 | Standard solder pins - inserted | 10 | 2.4 | 24 | PR 354904P | 12A2609008-708 | Yes | 10
DB9 Backshell | TE CONNECTIVITY / AMP | 5748676-1 | Newark | 87K0249 | Zinc Allot with multiple cable clamps | 10 | 4.28 | 42.8 | PR 354904P | 12A2609008-708 | Yes | 7
CPC Male Connectors | TE CONNECTIVITY / AMP | 206434-1 | Newark | 46F1124 | 8 Pin male - JLAB_FREESTK 010315387 | 5 | 0 |  | Jlab | N/A | Yes | 17
CPC Cable Clamp | TE CONNECTIVITY / AMP | 206358-5 | Newark | 71K0405 | CABLE CLAMP, SIZE 11 | 5 | 3.9 | 19.5 | PR 354904P | 12A2609008-708 | Yes | 9
CPC Pins | TE CONNECTIVITY / AMP | 66506-9 - D | Newark | 98F7062 | 24-20AWG | 50 | 0.188 | 9.4 | PR 354904P | 12A2609008-708 | Yes | 11
CPC Pins | TE CONNECTIVITY / AMP | 1-66103-8 | Newark | 52K3323 | 24-20AWG | 50 | 0.242 | 12.1 | PR 354904P | 12A2609008-708 | Yes | 12
Extension Cable Pins | TE CONNECTIVITY / AMP | 1-794613-2 | Newark | 10M9837 | 26 - 30 AWG Pin | 400 | 0.09 | 36 | PR 354904P | 12A2609008-708 | Yes | 8
Slow Controls | Alpha Wire | 86302CY SL005 | Digi-key | 86302CY SL005-ND | 2 conductor, Slate, 22 AWG, braided and foil - 100' | 5 | 198.99 | 994.95 | PR 354904P | 12A2609008-708 | Yes | 2
Extension Cable Conn. | TE CONNECTIVITY / AMP | 1-794616-4 | Digi-key | A30275-ND | Female | 25 | 0.864 | 21.6 | PR 354904P | 12A2609008-708 | Yes | 4
Extension Cable Conn. | TE CONNECTIVITY / AMP | 1-794617-4 | Digi-key | A30299-ND | Male 14 conductor | 25 | 0.578 | 14.45 | PR 354904P | 12A2609008-708 | Yes | 5
Extension Cable Pins | TE CONNECTIVITY / AMP | 1-794611-2 | Digi-key | A33279-ND | 26 - 30 AWG Socket | 400 | 0.112 | 44.8 | PR 354904P | 12A2609008-708 | Yes | 6
Leak Sensor Extension | Alpha Wire | 3233 SL005 | Digikey | A3233-100-ND | 4 conductor, 16 AWG, shielded, 100' | 1 | 310.04 | 310.04 | PR 354904P | 12A2609008-708 | Yes | 3
DELL PRECISION T5810 computer | Dell | 701510005 | DELL | 701510005 | Desktop Computer | 1 | 1682.74 | 1682.74 | PR 354904P | PO 15-M1037 | Yes
RTD (4-wire) | Omega | EXTT-4CU-26S | Omega | EXTT-4CU-26S | 100' Spool | 1 | 123 | 123 | PR 354847 | 15-M0994-0 | YES
RTD (3-Wire) | Omega | EXTT-3CU-26S | Omega | EXTT-3CU-26S | 100' Spool | 1 | 114 | 114 | PR 354847 | 15-M0994-0 | YES | 18
Power Supply | Rhino | PSP05-DC24-5 | Automation Direct | PSP05-DC24-5 | DC CONVERTER 18-75VDC IN 5VDC OUT 5A DIN-RAIL PLAS CASE | 1 | 79 | 79 | PR 354879 | Credit Card-0 | Yes | 1
Key Switch | Allen Bradley | 800T-H33B | PLC Center | 800T-H33B | make before break switch | 2 | 124.5 | 249 | PR 354881 | Credit Card-0 | YES
Video Cables | Show Me Cables | 660-50 BL | Show Me Cables | 660-50 BL | Video +600MHz - 50' | 2 | 27.49 | 54.98 | PR 354882 | CREDITCARD-0 | Yes | N/A
National Instruments | National Instruments | NI 9217 | National Instruments | NI 9217 | 4 Channel RTD Module & Hardware | 1 | 630 | 630 | PR 354903 | 15-M0987-0 | Yes | N/A
[7 empty] | Total | 4995.73

## Cable Assemblies
SVT Hardware Interlock System Interconnect Assemblies
# | Cable Assembly Name | Hall B System QTY | Test System QTY | Spare QTY | Total Qty | Instrumentation (End 1) | Instrumentation (End 2) | Connector on Instrumentation (End 1) | Connector on Instrumentation (End 2) | Cable Connector End 1 Type | Cable Connector End 2 Type | Cable Type | Cable Assembly Length | Parts Status | Comments | Cable Construction Status | Type # | T1 Total Length (Ft) | Type # | Total Length (Ft)
1 | HFCB Temperature Cable Assemblies | 4 | 1 | 1 | 6 | SVT Patch Panel Terminal Block with screw terminals | cRio NI 3929 4 Ch Isolated ADC | Terminal Block screw connection | Screw connector on NI Module | Crimped Ferrules | Crimped Ferrules | 2 conductors used - shielded - SVT SC cable type | 10 ft. | Have All Parts | Shares screw terminal block connections with the EPICS System | Not Started | 1 | 60
2 | Detector Temperature Cable Extension Assemblies | 3 | 1 | 2 | 6 | 4 wire RTD cable (disconnected from terminal block) | cRio NI 9216 8 Ch RTD module | Mating male sensor board connector or equivalent | Spring terminal on NI Module | Mating Female sensor board connector or equivalent | Crimped Ferrules - strip back white insolation ~ 3" | Omega 4 wire RTD cable (same as SVT) | 10 ft. | Have All Parts | Disconnect white RTD cable from terminal block, remove ferrules and add connectors | Not Started |  |  | 2 | 120
3 | Detector Humidity Cable Extension Assemblies | 3 | 1 | 2 | 6 | 3 wire RTD cable (disconnected from terminal block) | cRio NI 9205 16 CH Diff ADC, +5V term, GND term | Mating male sensor board connector or equivalent | Spring terminal on NI Module | Mating Female sensor board connector or equivalent | Crimped Ferrules - strip back white insolation ~ 12" | Omega 3 wire RTD cable (same as SVT) | 10 ft. | Have All Parts | Disconnect white RTD cable from terminal block, remove ferrules and add connectors. SEE WIRING DIAGRAM additional hookup wire needed from GND to ADC | Not Started |  |  | 3 | 120
4 | Ambient Temperature Cable Assemblies | 2 | 1 | 2 | 5 | SVT Temp / Humidity PCB Assembly | cRio NI 9216 8 Ch RTD module | None - Soldered to SVT Temp / Humidity PCB Assembly | Spring terminal on NI Module | None | Crimped Ferrules - strip back white insolation ~ 3" | Omega 4 wire RTD cable (same as SVT) | 10 ft. | Sensor board and cable assembly on hand- Need to strip back white insolation ~ 3" | Uses same cable assembly as cable type #5 Temp & Humidity | Sensor board and cable assembly on hand- Need to strip back white insolation ~ 3" | N/A
5 | Ambient Humidity Cable Assemblies | 2 | 1 | 2 | 5 | SVT Temp / Humidity PCB Assembly | cRio NI 9205 16 CH Diff ADC, +5V term, GND term | None - Soldered to SVT Temp / Humidity PCB Assembly | Spring terminal on NI Module | None | Crimped Ferrules - strip back white insolation ~ 12" | Omega 3 wire RTD cable (same as SVT) | 10 ft. | Sensor board and cable assembly on hand- Need to strip back white insolation ~ 12" | Uses same cable assembly as cable type #4 Temp & Humidity. SEE WIRING DIAGRAM additional hookup wire needed from GND to ADC | Sensor board and cable assembly on hand- Need to strip back white insolation ~ 12" | N/A
6 | Coolant Flow Cable Assemblies | 2 | 1 | 1 | 4 | SVT Patch Panel Terminal Block with screw terminals | cRio NI 9205 16 CH Diff ADC | Terminal Block screw connection | Spring terminal on NI Module | Crimped Ferrules | Crimped Ferrules | 2 conductors used - shielded - SVT SC cable type | 10 ft. | Have All Parts | Shares screw terminal block connections with the EPICS System | Not Started | 1 | 40
7 | Coolant Temperature Cable Assemblies | 1 | 1 | 1 | 3 | SVT Patch Panel Terminal Block with screw terminals | cRio NI 9205 16 CH Diff ADC | Terminal Block screw connection | Spring terminal on NI Module | Crimped Ferrules | Crimped Ferrules | 2 conductors used - shielded - SVT SC cable type | 10 ft. | Have All Parts | Shares screw terminal block connections with the EPICS System | Not Started | 1 | 30
8 | Coolant Leak Detection - Type 1 - Outputs Cable Assemblies | 2 | 1 | 1 | 4 | Panasonic Leak Controller Module in Hardware Interlock Chassis | cRio NI 9205 16 CH Diff ADC | Spring Terminal on Panasonic Leak Controller | Spring terminal on NI Module | Crimped Ferrules | Crimped Ferrules | 2 conductors used - shielded - SVT SC cable type | 10 ft. | Have All Parts | Output connections on Panasonic Controller - Y1 - 24V when leak fault, and Aux 1 - ~123 mV on fault | Not Started | 1 | 40
9 | Coolant Leak Detection - Type 2 - Sensor Cable Extension Assemblies | 1 | 1 | 1 | 3 | Leak Sensor Assembly | Panasonic Leak Controller Module in Hardware Interlock Chassis | None -Molded Assembly on leak Sensor | 4 Pin Female socket | None | Sensor IDC crimp connectors | 4 conductors - Use same wire from manufacturer | TBD (check length to dip tray) | Have All Parts | Solder an extension onto existing sensor cables from Ramco Innovations/SunxSensors.com | Not Started |  |  | 4 | 50
10 | Coolant Leak Detection - Type 3 - Power Cable Assembly | 1 | 0 | 0 | 1 | Panasonic Leak Controller Module in Hardware Interlock Chassis | To +24V & GND Power terminals in Hardware Interlock Chassis | Spring Terminal on Panasonic Leak Controller | Screw Terminal on Power Terminals | Larger (Power) Crimped Ferrules | Larger (Power) Crimped Ferrules | 16 AWG (26/36) PVC hookup wire - Red & Black | see chassis | Have All Parts | Connects to + 24V power block terminals (Allen Bradley) | Not Started | N/A
11 | Coolant Leak Detection - Type 4 - Reset Cable Assembly | 1 | 0 | 0 | 1 | Panasonic Leak Controller Module in Hardware Interlock Chassis | cRio NI 9485 8 CH Solid State Relay | Spring Terminal on Panasonic Leak Controller | Screw Terminal on NI Module | Crimped Ferrules | Crimped Ferrules | 22 AWG PVC hookup wire - Black | see chassis | Have All Parts | Reset terminals on Panasonic Controller - X1 and X1 on center connector | Not Started | N/A
12 | Mpod Crate Enable Cable Assemblies | 5 | 1 | 2 | 8 | Mpod Crate Controllers | cRio NI 9485 8 CH Solid State Relay, +5V term, GND term | 9 Pin D Female connector | Screw Terminal on NI Module, Screw Terminals on Power | 9 Pin D Male connector with backshell | Crimped Ferrules | 2 conductors used - shielded - SVT SC cable type, Also 22 AWG PVC hookup wire - Red | 10 ft. | Have All Parts | Connects NI Relay and to +5V power block terminals (Allen Bradley) | Not Started | 1 | 80
13 | Chiller Disable Cable Assembly | 1 | 0 | 1 | 2 | BiRa AC Power Reset Module | cRio NI 9485 8 CH Solid State Relay, +24V term, GND term | 8 pin Female CPC Connector | Screw Terminal on NI Module, Screw Terminals on Power | 8 pin Male CPC Connector | Crimped Ferrules | 8 Conductor - Grey Control Cable | 100 ft | Have All Parts | Connects NI Relay and to +24V power block terminals (Allen Bradley) CPC pin # 6 (+24V coil), Pin 7 ( - Coil GND) | Not Started |  |  | 5 | 200
[5 empty] | 54 | Cable Assemblies | [8 empty] | Cable Type 1 - SVT SC cable 2/4 conductor- Grey | 500 |  | 250
[15 empty] | Cable Type 2 - Omega 4 Wire RTD Cable | 120
[15 empty] | Cable Type 3 - Omega 3 Wire RTD Cable | 120
[15 empty] | Cable Type 4 - Sensor Extension Cable | 50
[15 empty] | Cable Type 5 - 8 Conductor Grey Control Cable | 200

## cRio Module Assignments
SVT Hardware Interlock System Channel Assignments
| Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
Channel | NI 9239 ADC | Empty | NI 9217 RTD | NI 9217 RTD | NI 9239 ADC | NI 9205 ADC | Empty | NI 9485 Relay
Ch 0 | HFCB R1 M1 - Top |  | Detector Temp (R2) | Ambient Temperature 1 | Coolant Flow Outlet | Detector Humidity (R2) |  | Mpod Crate 1 Enable
Ch 1 | HFCB R2 M1 - Top |  | Detector Temp (R3) | Ambient Temperature 2 | Coolant Flow Inlet | Detector Humidity (R3) |  | Mpod Crate 2 Enable
Ch 2 | HFCB R3 M1 - Top |  | Detector Temp (R4) | Spare | Coolant Temp | Detector Humidity (R4) |  | Mpod Crate 3 Enable
Ch 3 | HFCB R4 M1 - Top |  | Spare | Spare | Coolant Leak 1 | Ambient Humidity 1 |  | Mpod Crate 4 Enable
Ch 4 | Slot 6: Ambient Humidity 2; Slot 8: Mpod Crate 5 Enable
Ch 5 | Slot 6: Spare; Slot 8: Chiller Disable
Ch 6 | Slot 6: Spare; Slot 8: Water Leak Reset
Ch 7 | Slot 6: Spare; Slot 8: Spare
Ch 8 | Slot 6: Spare (CH16)
Ch 9 | Slot 6: Spare (CH17)
Ch 10 | Slot 6: +5V Supply Monitor (Ch18)
Ch 11 | Slot 6: Mpod +5V Override (CH19)
Ch 12 | Slot 6: Chiller Override (CH20)
Ch 13 | Slot 6: Spare (CH21)
Ch 14 | [5 empty] | Spare (CH22) |  |  | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
Ch 15 | [5 empty] | Spare (CH23) |  |  | NI 9239 | Empty | NI 9217 | NI 9217 | NI 9239 | NI 9205 | Empty | NI 9485
cRio Module Description
NI 9239 (4) channel Isolated +/-10V ADC, 24 bit resolution
NI 9217 (4) Channel RTD module, 100 ohms, 3 or 4 wire, 24 bit resolution
| Signal Name | Number of Channels | Input / Output | Description |  |  |  |  | Slot 1: NI 9205 (16) Differential Channels, +/- 200mV to +/- 10V, 16 bit resolution
| HFCB Temperature | 4 | Analog Inputs | Monitors top side of a subset of modules in R1, R2, R3, R4 |  |  |  |  | Slot 1: NI 9485 (8) Channel Solid State Relay module, 60VDC, 750 mA, isolated channels
| Detector Internal Temperature | 3 | RTD Inputs | RTD’s are mounted in the support rings, The Hardware Interlock System will use the backup sensors (to be disconnected in EPICS).
| Detector Internal Humidity / Dew Point | 3 | Analog Inputs | Humidity sensors are mounted in the support rings, The Hardware Interlock System will use the backup sensors (to be disconnected in EPICS).
| Ambient Temperature | 2 | RTD Inputs | RTD’s are mounted externally to the detector.
| Ambient Humidity / Dew Point | 2 | Analog Inputs | Humidity sensors are mounted externally to the detector.
| Coolant Flow | 2 | Analog Inputs | Measures coolant flow (external from chiller) (R1-3) + (R4)
| Coolant Temperature | 1 | Analog Input | Measures coolant temperature (external from chiller)
| Coolant Leak Detection | 1 | Analog Input | Checks for coolant leaks via sensor mounted in drip pan.
| +5V supply Monitor | 1 | Analog Input | Checks +5V supply for humidity sensors and Mpod crate enable
| Mpod +5V Override | 1 | Analog Input | Checks if Mpod crate override is enabled
| Chiller Override | 1 | Analog Input | Checks if Chiller override is enabled
| Water leak Reset | 1 | Relay | Resets water leak sensor
| Chiller Disable | 1 | Relay | Signal to BiRa AC Unit - Removes 120VAC from Chiller.
| Mpod HV/LV Crate Disable | 5 | Relay | Signals to Mpod crate controllers to ramp down LV & HV

## FT EPICS Interface
Hall B FT Hardware Interlock System EPICS Interface
Signal Category | LabVIEW Signal Name | Access Type | Data Type | Server EPICS Process Variable (PV) | EPICS Process Variable (PV) | LabVIEW EPICS Process Variable (PV) | Units | PV # | Group #
Signal Monitoring | FT EPICS Calorimeter Temp #1 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_1 | B_DET_FTC_INTLK_TEMP1 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1\VAL | °C | 1 | 1
| FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\FT EPICS Calorimeter Temp #2 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_2 | B_DET_FTC_INTLK_TEMP2 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2\VAL | °C | 2 | 2
| FT EPICS Calorimeter Temp #3 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_3 | B_DET_FTC_INTLK_TEMP3 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3\VAL | °C | 3 | 3
| FT EPICS Calorimeter Temp #4 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_4 | B_DET_FTC_INTLK_TEMP4 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4\VAL | °C | 4 | 4
| FT EPICS Calorimeter Temp #5 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_5 | B_DET_FTC_INTLK_TEMP5 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5\VAL | °C | 5 | 5
| FT EPICS Calorimeter Temp #6 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_6 | B_DET_FTC_INTLK_TEMP6 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6\VAL | °C | 6 | 6
| FT EPICS Hodoscope Temp #1 | Read Only | Double | B_FT_INTERLOCKS_HODO_TEMP_1 | B_DET_FTH_INTLK_TEMP1 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1\VAL | °C | 7 | 7
| FT EPICS Hodoscope Temp #2 | Read Only | Double | B_FT_INTERLOCKS_HODO_TEMP_2 | B_DET_FTH_INTLK_TEMP2 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2\VAL | °C | 8 | 8
| FT EPICS Calorimeter Humidity #1 | Read Only | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1 | B_DET_FTC_INTLK_HUMID1 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1\VAL | %RH | 9 | 9
| FT EPICS Calorimeter Humidity #2 | Read Only | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2 | B_DET_FTC_INTLK_HUMID2 | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2\VAL | %RH | 10 | 10
| FT EPICS Calorimeter Gas Flow | Read Only | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW | B_DET_FTC_INTLK_FLOW | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW\VAL | sccm | 11 | 11
Individual Sensor Interlock Status | FT EPICS Cal Temp 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_HI_STATUS | B_DET_FTC_INTLK_TEMP1_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_HI_STAT\VAL | N/A | 12 | 1
| FT EPICS Cal Temp 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LO_STATUS | B_DET_FTC_INTLK_TEMP1_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_LO_STAT\VAL | N/A | 13 | 2
| FT EPICS Cal Temp 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_HI_STATUS | B_DET_FTC_INTLK_TEMP2_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_HI_STAT\VAL | N/A | 14 | 3
| FT EPICS Cal Temp 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LO_STATUS | B_DET_FTC_INTLK_TEMP2_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_LO_STAT\VAL | N/A | 15 | 4
| FT EPICS Cal Temp 3 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_HI_STATUS | B_DET_FTC_INTLK_TEMP3_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_HI_STAT\VAL | N/A | 16 | 5
| FT EPICS Cal Temp 3 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LO_STATUS | B_DET_FTC_INTLK_TEMP3_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_LO_STAT\VAL | N/A | 17 | 6
| FT EPICS Cal Temp 4 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_HI_STATUS | B_DET_FTC_INTLK_TEMP4_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_HI_STAT\VAL | N/A | 18 | 7
| FT EPICS Cal Temp 4 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LO_STATUS | B_DET_FTC_INTLK_TEMP4_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_LO_STAT\VAL | N/A | 19 | 8
| FT EPICS Cal Temp 5 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_HI_STATUS | B_DET_FTC_INTLK_TEMP5_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_HI_STAT\VAL | N/A | 20 | 9
| FT EPICS Cal Temp 5 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LO_STATUS | B_DET_FTC_INTLK_TEMP5_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_LO_STAT\VAL | N/A | 21 | 10
| FT EPICS Cal Temp 6 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_HI_STATUS | B_DET_FTC_INTLK_TEMP6_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_HI_STAT\VAL | N/A | 22 | 11
| FT EPICS Cal Temp 6 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LO_STATUS | B_DET_FTC_INTLK_TEMP6_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_LO_STAT\VAL | N/A | 23 | 12
| FT EPICS Hodo Temp 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_HI_STATUS | B_DET_FTH_INTLK_TEMP1_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_HI_STAT\VAL | N/A | 24 | 13
| FT EPICS Hodo Temp 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LO_STATUS | B_DET_FTH_INTLK_TEMP1_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_LO_STAT\VAL | N/A | 25 | 14
| FT EPICS Hodo Temp 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_HI_STATUS | B_DET_FTH_INTLK_TEMP2_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_HI_STAT\VAL | N/A | 26 | 15
| FT EPICS Hodo Temp 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LO_STATUS | B_DET_FTH_INTLK_TEMP2_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_LO_STAT\VAL | N/A | 27 | 16
| FT EPICS Cal Humidity 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_HI_STATUS | B_DET_FTC_INTLK_HUMID1_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_HI_STAT\VAL | N/A | 28 | 17
| FT EPICS Cal Humidity 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LO_STATUS | B_DET_FTC_INTLK_HUMID1_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_LO_STAT\VAL | N/A | 29 | 18
| FT EPICS Cal Humidity 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_HI_STATUS | B_DET_FTC_INTLK_HUMID2_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_HI_STAT\VAL | N/A | 30 | 19
| FT EPICS Cal Humidity 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LO_STATUS | B_DET_FTC_INTLK_HUMID2_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_LO_STAT\VAL | N/A | 31 | 20
| FT EPICS Cal Gas Flow 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_HI_STATUS | B_DET_FTC_INTLK_FLOW_HI_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_HI_STAT\VAL | N/A | 32 | 21
| FT EPICS Cal Gas Flow 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LO_STATUS | B_DET_FTC_INTLK_FLOW_LO_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_LO_STAT\VAL | N/A | 33 | 22
Sum of Calorimeter Interlocks Status | FT EPICS Any Calorimeter Interlocks Over Limit? | Read Only | Boolean | B_FT_INTERLOCKS_ANY_CALORIMETER_INTERLOCKS_OVER_LIMIT | B_DET_FTC_INTLK_ANY_OVERLIMIT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_ANY_OVERLIMIT\VAL | N/A | 34 | 1
Sum of Calorimeter Temperature Status | FT EPICS Calorimeter Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_TEMPERATURE_STATUS | B_DET_FTC_INTLK_TEMP_STATUS | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP_STATUS\VAL | N/A | 35 | 1
Sum of Calorimeter Humidity Status | FT EPICS Calorimeter Humidity Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_HUMIDITY_STATUS | B_DET_FTC_INTLK_HUMID_STATUS | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID_STATUS\VAL | N/A | 36 | 1
Sum of Calorimeter Gas Flow Status | FT EPICS Calorimeter Gas Flow Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_GAS_FLOW_STATUS | B_DET_FTC_INTLK_FLOW_STATUS | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_STATUS\VAL | N/A | 37 | 1
Sum of Hodoscope Interlocks Status | FT EPICS Any Hodoscope Interlocks Over Limit? | Read Only | Boolean | B_FT_INTERLOCKS_ANY_HODOSCOPE_INTERLOCKS_OVER_LIMIT | B_DET_FTH_INTLK_ANY_OVERLIMIT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_ANY_OVERLIMIT\VAL | N/A | 38 | 1
Sum of Hodoscope Temperature Status | FT EPICS Hodoscope Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_TEMPERATURE_STATUS | B_DET_FTH_INTLK_TEMP_STATUS | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP_STATUS\VAL | N/A | 39 | 1
Individual Sensor Latched Errors | FT EPICS Cal Temp 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP1_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_LATCHED_HI_ERR\VAL | N/A | 40 | 1
| FT EPICS Cal Temp 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP1_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_LATCHED_LO_ERR\VAL | N/A | 41 | 2
| FT EPICS Cal Temp 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP2_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_LATCHED_HI_ERR\VAL | N/A | 42 | 3
| FT EPICS Cal Temp 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP2_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_LATCHED_LO_ERR\VAL | N/A | 43 | 4
| FT EPICS Cal Temp 3 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP3_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_LATCHED_HI_ERR\VAL | N/A | 44 | 5
| FT EPICS Cal Temp 3 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP3_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_LATCHED_LO_ERR\VAL | N/A | 45 | 6
| FT EPICS Cal Temp 4 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP4_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_LATCHED_HI_ERR\VAL | N/A | 46 | 7
| FT EPICS Cal Temp 4 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP4_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_LATCHED_LO_ERR\VAL | N/A | 47 | 8
| FT EPICS Cal Temp 5 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP5_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_LATCHED_HI_ERR\VAL | N/A | 48 | 9
| FT EPICS Cal Temp 5 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP5_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_LATCHED_LO_ERR\VAL | N/A | 49 | 10
| FT EPICS Cal Temp 6 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LATCHED_HI_ERROR | B_DET_FTC_INTLK_TEMP6_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_LATCHED_HI_ERR\VAL | N/A | 50 | 11
| FT EPICS Cal Temp 6 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LATCHED_LO_ERROR | B_DET_FTC_INTLK_TEMP6_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_LATCHED_LO_ERR\VAL | N/A | 51 | 12
| FT EPICS Hodo Temp 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LATCHED_HI_ERROR | B_DET_FTH_INTLK_TEMP1_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_LATCHED_HI_ERR\VAL | N/A | 52 | 13
| FT EPICS Hodo Temp 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LATCHED_LO_ERROR | B_DET_FTH_INTLK_TEMP1_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_LATCHED_LO_ERR\VAL | N/A | 53 | 14
| FT EPICS Hodo Temp 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LATCHED_HI_ERROR | B_DET_FTH_INTLK_TEMP2_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_LATCHED_HI_ERR\VAL | N/A | 54 | 15
| FT EPICS Hodo Temp 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LATCHED_LO_ERROR | B_DET_FTH_INTLK_TEMP2_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_LATCHED_LO_ERR\VAL | N/A | 55 | 16
| FT EPICS Cal Humidity 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LATCHED_HI_ERROR | B_DET_FTC_INTLK_HUMID1_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_LATCHED_HI_ERR\VAL | N/A | 56 | 17
| FT EPICS Cal Humidity 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LATCHED_LO_ERROR | B_DET_FTC_INTLK_HUMID1_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_LATCHED_LO_ERR\VAL | N/A | 57 | 18
| FT EPICS Cal Humidity 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LATCHED_HI_ERROR | B_DET_FTC_INTLK_HUMID2_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_LATCHED_HI_ERR\VAL | N/A | 58 | 19
| FT EPICS Cal Humidity 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LATCHED_LO_ERROR | B_DET_FTC_INTLK_HUMID2_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_LATCHED_LO_ERR\VAL | N/A | 59 | 20
| FT EPICS Cal Gas Flow 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_HI_ERROR | B_DET_FTC_INTLK_FLOW_LATCHED_HI_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_LATCHED_HI_ERR\VAL | N/A | 60 | 21
| FT EPICS Cal Gas Flow 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_LO_ERROR | B_DET_FTC_INTLK_FLOW_LATCHED_LO_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_LATCHED_LO_ERR\VAL | N/A | 61 | 22
Sum of Calorimeter Temperature Latched Errors | FT EPICS Calorimeter Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMPERATURE_LATCHED_ERROR | B_DET_FTC_INTLK_TEMP_LATCHED_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP_LATCHED_ERR\VAL | N/A | 62 | 1
Sum of Calorimeter Humidity Latched Errors | FT EPICS Calorimeter Humidity Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_LATCHED_ERROR | B_DET_FTC_INTLK_HUMID_LATCHED_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID_LATCHED_ERR\VAL | N/A | 63 | 1
Sum of Calorimeter Gas Flow Latched Errors | FT EPICS Calorimeter Gas Flow Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_ERROR | B_DET_FTC_INTLK_FLOW_LATCHED_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_LATCHED_ERR\VAL | N/A | 64 | 1
Sum of Hodoscope Temperature Latched Errors | FT EPICS Hodoscope Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMPERATURE_LATCHED_ERROR | B_DET_FTH_INTLK_TEMP_LATCHED_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP_LATCHED_ERR\VAL | N/A | 65 | 1
Reset of All Latched Errors | FT EPICS Reset Latched Errors | Read/Write | Boolean | B_FT_INTERLOCKS_RESET_LATCHED_ERRORS | B_DET_FT_INTLK_RESET_LATCHED_ERR | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FT_INTLK_RESET_LATCHED_ERR\VAL | N/A | 66 | 1
Individual Sensor Interlock Enables | FT EPICS Calorimeter Temp #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP1_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_ENABLE\VAL | N/A | 67 | 1
| FT EPICS Calorimeter Temp #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP2_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_ENABLE\VAL | N/A | 68 | 2
| FT EPICS Calorimeter Temp #3 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP3_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_ENABLE\VAL | N/A | 69 | 3
| FT EPICS Calorimeter Temp #4 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP4_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_ENABLE\VAL | N/A | 70 | 4
| FT EPICS Calorimeter Temp #5 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP5_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_ENABLE\VAL | N/A | 71 | 5
| FT EPICS Calorimeter Temp #6 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_INTERLOCK_ENABLE | B_DET_FTC_INTLK_TEMP6_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_ENABLE\VAL | N/A | 72 | 6
| FT EPICS Hodoscope Temp #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_INTERLOCK_ENABLE | B_DET_FTH_INTLK_TEMP1_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_ENABLE\VAL | N/A | 73 | 7
| FT EPICS Hodoscope Temp #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_INTERLOCK_ENABLE | B_DET_FTH_INTLK_TEMP2_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_ENABLE\VAL | N/A | 74 | 8
| FT EPICS Calorimeter Humidity #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_INTERLOCK_ENABLE | B_DET_FTC_INTLK_HUMID1_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_ENABLE\VAL | N/A | 75 | 9
| FT EPICS Calorimeter Humidity #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_INTERLOCK_ENABLE | B_DET_FTC_INTLK_HUMID2_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_ENABLE\VAL | N/A | 76 | 10
| FT EPICS Calorimeter Gas Flow Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_INTERLOCK_ENABLE | B_DET_FTC_INTLK_FLOW_ENABLE | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_ENABLE\VAL | N/A | 77 | 11
Individual Sensor Threshold Controls | FT EPICS Calorimeter Temp #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_1_HI_THRES | B_DET_FTC_INTLK_TEMP1_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_HI\VAL | °C | 78 | 1
| FT EPICS Calorimeter Temp #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_1_LO_THRES | B_DET_FTC_INTLK_TEMP1_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP1_LO\VAL | °C | 79 | 2
| FT EPICS Calorimeter Temp #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_2_HI_THRES | B_DET_FTC_INTLK_TEMP2_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_HI\VAL | °C | 80 | 3
| FT EPICS Calorimeter Temp #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_2_LO_THRES | B_DET_FTC_INTLK_TEMP2_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP2_LO\VAL | °C | 81 | 4
| FT EPICS Calorimeter Temp #3 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_3_HI_THRES | B_DET_FTC_INTLK_TEMP3_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_HI\VAL | °C | 82 | 5
| FT EPICS Calorimeter Temp #3 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_3_LO_THRES | B_DET_FTC_INTLK_TEMP3_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP3_LO\VAL | °C | 83 | 6
| FT EPICS Calorimeter Temp #4 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_4_HI_THRES | B_DET_FTC_INTLK_TEMP4_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_HI\VAL | °C | 84 | 7
| FT EPICS Calorimeter Temp #4 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_4_LO_THRES | B_DET_FTC_INTLK_TEMP4_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP4_LO\VAL | °C | 85 | 8
| FT EPICS Calorimeter Temp #5 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_5_HI_THRES | B_DET_FTC_INTLK_TEMP5_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_HI\VAL | °C | 86 | 9
| FT EPICS Calorimeter Temp #5 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_5_LO_THRES | B_DET_FTC_INTLK_TEMP5_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP5_LO\VAL | °C | 87 | 10
| FT EPICS Calorimeter Temp #6 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_6_HI_THRES | B_DET_FTC_INTLK_TEMP6_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_HI\VAL | °C | 88 | 11
| FT EPICS Calorimeter Temp #6 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_6_LO_THRES | B_DET_FTC_INTLK_TEMP6_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_TEMP6_LO\VAL | °C | 89 | 12
| FT EPICS Hodoscope Temp #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_1_HI_THRES | B_DET_FTH_INTLK_TEMP1_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_HI\VAL | °C | 90 | 13
| FT EPICS Hodoscope Temp #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_1_LO_THRES | B_DET_FTH_INTLK_TEMP1_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP1_LO\VAL | °C | 91 | 14
| FT EPICS Hodoscope Temp #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_2_HI_THRES | B_DET_FTH_INTLK_TEMP2_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_HI\VAL | °C | 92 | 15
| FT EPICS Hodoscope Temp #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_2_LO_THRES | B_DET_FTH_INTLK_TEMP2_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_TEMP2_LO\VAL | °C | 93 | 16
| FT EPICS Calorimeter Humidity #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1_HI_THRES | B_DET_FTC_INTLK_HUMID1_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_HI\VAL | %RH | 94 | 17
| FT EPICS Calorimeter Humidity #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LO_THRES | B_DET_FTC_INTLK_HUMID1_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID1_LO\VAL | %RH | 95 | 18
| FT EPICS Calorimeter Humidity #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2_HI_THRES | B_DET_FTC_INTLK_HUMID2_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_HI\VAL | %RH | 96 | 19
| FT EPICS Calorimeter Humidity #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LO_THRES | B_DET_FTC_INTLK_HUMID2_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HUMID2_LO\VAL | %RH | 97 | 20
| FT EPICS Calorimeter Gas Flow Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW_HI_THRES | B_DET_FTC_INTLK_FLOW_HI | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_HI\VAL | sccm | 98 | 21
| FT EPICS Calorimeter Gas Flow Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW_LO_THRES | B_DET_FTC_INTLK_FLOW_LO | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_FLOW_LO\VAL | sccm | 99 | 22
Threshold Control Status | FT EPICS Threshold Control | Read Only | Boolean | B_FT_INTERLOCKS_EPICS_THRESHOLD_CONTROL | B_DET_FT_INTLK_EPICS_THRESH_CTRL | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FT_INTLK_EPICS_THRESH_CTRL\VAL | N/A | 100 | 1
Hardware Interlock Status | FT EPICS Calorimeter LV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_LV_ENABLE_STATUS | B_DET_FTC_INTLK_LV_ENABLE_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_LV_ENABLE_STAT\VAL | N/A | 101 | 1
| FT EPICS Calorimeter HV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_HV_ENABLE_STATUS | B_DET_FTC_INTLK_HV_ENABLE_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_HV_ENABLE_STAT\VAL | N/A | 102 | 2
| FT EPICS Calorimeter Chiller Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_CHILLER_ENABLE_STATUS | B_DET_FTC_INTLK_CHILLER_ENABLE_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTC_INTLK_CHILLER_ENABLE_STAT\VAL | N/A | 103 | 3
| FT EPICS Hodoscope LV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_LV_ENABLE_STATUS | B_DET_FTH_INTLK_LV_ENABLE_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_LV_ENABLE_STAT\VAL | N/A | 104 | 4
| FT EPICS Hodoscope HV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_HV_ENABLE_STATUS | B_DET_FTH_INTLK_HV_ENABLE_STAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_DET_FTH_INTLK_HV_ENABLE_STAT\VAL | N/A | 105 | 5
Interlock System Status | FT EPICS cRio Heartbeat | Read Only | Boolean | B_FT_INTERLOCKS_CRIO_HEARTBEAT | B_HW_CRIO_FT_HEARTBEAT | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_HW_CRIO_FT_HEARTBEAT\VAL | N/A | 106 | 1
| FT EPICS cRio CPU Usage | Read Only | Double | B_FT_INTERLOCKS_CRIO_CPU_USEAGE | B_HW_CRIO_FT_CPULOAD | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_HW_CRIO_FT_CPULOAD\VAL | % | 107 | 2
| FT EPICS System Uptime | Read Only | Double | B_FT_INTERLOCKS_SYSTEM_UPTIME | B_HW_CRIO_FT_UPTIME | FTCRIO\FT_EPICS_Variables.lvlib\EPICS Client1\B_HW_CRIO_FT_UPTIME\VAL | Sec | 108 | 3

## SVT EPICS Interface
Hall B SVT Hardware Interlock System EPICS Interface
Signal Category | LabVIEW Signal Name | Access Type | Data Type | EPICS Process Variable (PV) | Units | PV # | Group #
Signal Monitoring | SVT EPICS HFCB Temp R1 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1 | °C | 1 | 1
| SVT EPICS HFCB Temp R2 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2 | °C | 2 | 2
| SVT EPICS HFCB Temp R3 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3 | °C | 3 | 3
| SVT EPICS Detector Int Temp R2 | Read Only | Double | B_DET_SVT_INTLK_INT_TEMP_R2 | °C | 4 | 4
| SVT EPICS Detector Int Temp R3 | Read Only | Double | B_DET_SVT_INTLK_INT_TEMP_R3 | °C | 5 | 5
| SVT EPICS Ambient Temp 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_TEMP1 | °C | 6 | 6
| SVT EPICS Ambient Temp 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_TEMP2 | °C | 7 | 7
| SVT EPICS Det Internal Humidity R2 | Read Only | Double | B_DET_SVT_INTLK_INT_HUMID_R2 | %RH | 8 | 8
| SVT EPICS Det Internal Humidity R3 | Read Only | Double | B_DET_SVT_INTLK_INT_HUMID_R3 | %RH | 9 | 9
| SVT EPICS Det Internal Dew Point Alarm R2 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_ALM_R2 |  | 10 | 10
| SVT EPICS Det Internal Dew Point Alarm R3 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_ALM_R3 |  | 11 | 11
| SVT EPICS Ambient Humidity H1 | Read Only | Double | B_DET_SVT_INTLK_AMB_HUMID1 | %RH | 12 | 12
| SVT EPICS Ambient Humidity H2 | Read Only | Double | B_DET_SVT_INTLK_AMB_HUMID2 | %RH | 13 | 13
| SVT EPICS Ambient Dew Point Alarm 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP_ALM1 |  | 14 | 14
| SVT EPICS Ambient Dew Point Alarm 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP_ALM2 |  | 15 | 15
| SVT EPICS Outlet Coolant Flow | Read Only | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW | L/Min | 16 | 16
| SVT EPICS Inlet Coolant Flow | Read Only | Double | B_DET_SVT_INTLK_COOL_IN_FLOW | L/Min | 17 | 17
| SVT EPICS Coolant Temp | Read Only | Double | B_DET_SVT_INTLK_COOL_TEMP | °C | 18 | 18
| SVT EPICS Ambient Dew Point 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP1 |  | 19 | 19
| SVT EPICS Ambient Dew Point 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP2 |  | 20 | 20
| SVT EPICS Det Internal Dew Point R2 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_R2 |  | 21 | 21
| SVT EPICS Det Internal Dew Point R3 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_R3 |  | 22 | 22
Individual Sensor Interlock Status | SVT EPICS HFCB Temp R1 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_HI_STAT | N/A | 23 | 1
| SVT EPICS HFCB Temp R1 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LO_STAT | N/A | 24 | 2
| SVT EPICS HFCB Temp R2 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_HI_STAT | N/A | 25 | 3
| SVT EPICS HFCB Temp R2 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LO_STAT | N/A | 26 | 4
| SVT EPICS HFCB Temp R3 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_HI_STAT | N/A | 27 | 5
| SVT EPICS HFCB Temp R3 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LO_STAT | N/A | 28 | 6
| SVT EPICS Detector Int Temp R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_HI_STAT | N/A | 29 | 7
| SVT EPICS Detector Int Temp R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LO_STAT | N/A | 30 | 8
| SVT EPICS Detector Int Temp R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_HI_STAT | N/A | 31 | 9
| SVT EPICS Detector Int Temp R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LO_STAT | N/A | 32 | 10
| SVT EPICS Ambient Temp 1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_HI_STAT | N/A | 33 | 11
| SVT EPICS Ambient Temp 1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LO_STAT | N/A | 34 | 12
| SVT EPICS Ambient Temp 2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_HI_STAT | N/A | 35 | 13
| SVT EPICS Ambient Temp 2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LO_STAT | N/A | 36 | 14
| SVT EPICS Det Internal Humidity R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_HI_STAT | N/A | 37 | 15
| SVT EPICS Det Internal Humidity R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LO_STAT | N/A | 38 | 16
| SVT EPICS Det Internal Humidity R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_HI_STAT | N/A | 39 | 17
| SVT EPICS Det Internal Humidity R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LO_STAT | N/A | 40 | 18
| SVT EPICS Det Internal Dew Point R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_HI_STAT | N/A | 41 | 19
| SVT EPICS Det Internal Dew Point R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LO_STAT | N/A | 42 | 20
| SVT EPICS Det Internal Dew Point R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_HI_STAT | N/A | 43 | 21
| SVT EPICS Det Internal Dew Point R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LO_STAT | N/A | 44 | 22
| SVT EPICS Ambient Humidity H1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_HI_STAT | N/A | 45 | 23
| SVT EPICS Ambient Humidity H1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LO_STAT | N/A | 46 | 24
| SVT EPICS Ambient Humidity H2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_HI_STAT | N/A | 47 | 25
| SVT EPICS Ambient Humidity H2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LO_STAT | N/A | 48 | 26
| SVT EPICS Ambient Dew Point 1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_HI_STAT | N/A | 49 | 27
| SVT EPICS Ambient Dew Point 1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LO_STAT | N/A | 50 | 28
| SVT EPICS Ambient Dew Point 2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_HI_STAT | N/A | 51 | 29
| SVT EPICS Ambient Dew Point 2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LO_STAT | N/A | 52 | 30
| SVT EPICS Outlet Coolant Flow Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_HI_STAT | N/A | 53 | 31
| SVT EPICS Outlet Coolant Flow Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LO_STAT | N/A | 54 | 32
| SVT EPICS Inlet Coolant Flow Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_HI_STAT | N/A | 55 | 33
| SVT EPICS Inlet Coolant Flow Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LO_STAT | N/A | 56 | 34
| SVT EPICS Coolant Temp Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_HI_STAT | N/A | 57 | 35
| SVT EPICS Coolant Temp Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LO_STAT | N/A | 58 | 36
| SVT EPICS Coolant Leak Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_HI_STAT | N/A | 59 | 37
| SVT EPICS Coolant Leak Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LO_STAT | N/A | 60 | 38
Sum of Interlocks Status | SVT EPICS Any Interlock Over Limit? | Read Only | Boolean | B_DET_SVT_INTLK_ANY_OVERLIMIT | N/A | 61 | 1
Sum of Temperature Status | SVT EPICS Temperature Status | Read Only | Boolean | B_DET_SVT_INTLK_TEMP_STATUS | N/A | 62 | 1
Sum of Humidity Status | SVT EPICS Humidity Status | Read Only | Boolean | B_DET_SVT_INTLK_HUMID_STATUS | N/A | 63 | 1
Sum of Dew Point Status | SVT EPICS Dew Point Status | Read Only | Boolean | B_DET_SVT_INTLK_DEWP_STATUS | N/A | 64 | 1
Sum of Coolant Inlet Flow Status | SVT EPICS Inlet Coolant Flow Status | Read Only | Boolean | B_DET_SVT_INTLK_IN_FLOW_STATUS | N/A | 65 | 1
Sum of Coolant Outlet Flow Status | SVT EPICS Outlet Coolant Flow Status | Read Only | Boolean | B_DET_SVT_INTLK_OUT_FLOW_STATUS | N/A | 66 | 1
Sum of Coolant Temperature Status | SVT EPICS Coolant Temp Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_STATUS | N/A | 67 | 1
Individual Sensor Latched Errors | SVT EPICS HFCB Temp R1 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_HI_ERR | N/A | 68 | 1
| SVT EPICS HFCB Temp R1 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_LO_ERR | N/A | 69 | 2
| SVT EPICS HFCB Temp R2 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_HI_ERR | N/A | 70 | 3
| SVT EPICS HFCB Temp R2 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_LO_ERR | N/A | 71 | 4
| SVT EPICS HFCB Temp R3 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_HI_ERR | N/A | 72 | 5
| SVT EPICS HFCB Temp R3 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_LO_ERR | N/A | 73 | 6
| SVT EPICS Detector Int Temp R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_HI_ERR | N/A | 74 | 7
| SVT EPICS Detector Int Temp R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_LO_ERR | N/A | 75 | 8
| SVT EPICS Detector Int Temp R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_HI_ERR | N/A | 76 | 9
| SVT EPICS Detector Int Temp R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_LO_ERR | N/A | 77 | 10
| SVT EPICS Ambient Temp 1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_HI_ERR | N/A | 78 | 11
| SVT EPICS Ambient Temp 1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_LO_ERR | N/A | 79 | 12
| SVT EPICS Ambient Temp 2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_HI_ERR | N/A | 80 | 13
| SVT EPICS Ambient Temp 2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_LO_ERR | N/A | 81 | 14
| SVT EPICS Det Internal Humidity R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_HI_ERR | N/A | 82 | 15
| SVT EPICS Det Internal Humidity R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_LO_ERR | N/A | 83 | 16
| SVT EPICS Det Internal Humidity R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_HI_ERR | N/A | 84 | 17
| SVT EPICS Det Internal Humidity R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_LO_ERR | N/A | 85 | 18
| SVT EPICS Det Internal Dew Point R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_HI_ERR | N/A | 86 | 19
| SVT EPICS Det Internal Dew Point R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_LO_ERR | N/A | 87 | 20
| SVT EPICS Det Internal Dew Point R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_HI_ERR | N/A | 88 | 21
| SVT EPICS Det Internal Dew Point R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_LO_ERR | N/A | 89 | 22
| SVT EPICS Ambient Humidity H1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_HI_ERR | N/A | 90 | 23
| SVT EPICS Ambient Humidity H1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_LO_ERR | N/A | 91 | 24
| SVT EPICS Ambient Humidity H2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_HI_ERR | N/A | 92 | 25
| SVT EPICS Ambient Humidity H2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_LO_ERR | N/A | 93 | 26
| SVT EPICS Ambient Dew Point 1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_HI_ERR | N/A | 94 | 27
| SVT EPICS Ambient Dew Point 1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_LO_ERR | N/A | 95 | 28
| SVT EPICS Ambient Dew Point 2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_HI_ERR | N/A | 96 | 29
| SVT EPICS Ambient Dew Point 2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_LO_ERR | N/A | 97 | 30
| SVT EPICS Outlet Coolant Flow Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_HI_ERR | N/A | 98 | 31
| SVT EPICS Outlet Coolant Flow Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_LO_ERR | N/A | 99 | 32
| SVT EPICS Inlet Coolant Flow Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_HI_ERR | N/A | 100 | 33
| SVT EPICS Inlet Coolant Flow Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_LO_ERR | N/A | 101 | 34
| SVT EPICS Coolant Temp Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_HI_ERR | N/A | 102 | 35
| SVT EPICS Coolant Temp Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_LO_ERR | N/A | 103 | 36
| SVT EPICS Coolant Leak Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LATCHED_HI_ERR | N/A | 104 | 37
| SVT EPICS Coolant Leak Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LATCHED_LO_ERR | N/A | 105 | 38
Sum of Temperature Latched Errors | SVT EPICS Temperature Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_TEMP_LATCHED_ERR | N/A | 106 | 1
Sum of Humidity Latched Errors | SVT EPICS Humidity Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_HUMID_LATCHED_ERR | N/A | 107 | 1
Sum of Dew Point Latched Errors | SVT EPICS Dew Point Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_DEWP_LATCHED_ERR | N/A | 108 | 1
Sum Coolant Inlet Flow Latched Errors | SVT EPICS Inlet Coolant Flow Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_IN_FLOW_LATCHED_ERR | N/A | 109 | 1
Sum of Coolant Outlet Flow Latched Errors | SVT EPICS Outlet Coolant Flow Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_OUT_FLOW_LATCHED_ERR | N/A | 110 | 1
Sum of Coolant Temperature Latched Errors | SVT EPICS Coolant Temperature Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_ERR | N/A | 111 | 1
Reset of All Latched Errors | SVT EPICS Coolant Leak Latched Lo Error | Read/Write | Boolean | B_DET_SVT_INTLK_RESET_LATCHED_ERR | N/A | 112 | 1
Individual Sensor Interlock Enables | SVT EPICS HFCB Temp R1 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_ENABLE | N/A | 113 | 1
| SVT EPICS HFCB Temp R2 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_ENABLE | N/A | 114 | 2
| SVT EPICS HFCB Temp R3 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_ENABLE | N/A | 115 | 3
| SVT EPICS Detector Int Temp R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_ENABLE | N/A | 116 | 4
| SVT EPICS Detector Int Temp R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_ENABLE | N/A | 117 | 5
| SVT EPICS Ambient Temp 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_ENABLE | N/A | 118 | 6
| SVT EPICS Ambient Temp 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_ENABLE | N/A | 119 | 7
| SVT EPICS Det Internal Humidity R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_ENABLE | N/A | 120 | 8
| SVT EPICS Det Internal Humidity R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_ENABLE | N/A | 121 | 9
| SVT EPICS Det Internal Dew Point R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_ENABLE | N/A | 122 | 10
| SVT EPICS Det Internal Dew Point R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_ENABLE | N/A | 123 | 11
| SVT EPICS Ambient Humidity H1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_ENABLE | N/A | 124 | 12
| SVT EPICS Ambient Humidity H2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_ENABLE | N/A | 125 | 13
| SVT EPICS Ambient Dew Point 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_ENABLE | N/A | 126 | 14
| SVT EPICS Ambient Dew Point 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_ENABLE | N/A | 127 | 15
| SVT EPICS Outlet Coolant Flow Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_ENABLE | N/A | 128 | 16
| SVT EPICS Inlet Coolant Flow Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_ENABLE | N/A | 129 | 17
| SVT EPICS Coolant Temp Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_TEMP_ENABLE | N/A | 130 | 18
| SVT EPICS Coolant Leak 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_LEAK1_ENABLE | N/A | 131 | 19
| SVT EPICS Coolant Leak 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_LEAK2_ENABLE | N/A | 132 | 20
Individual Sensor Threshold Controls | SVT EPICS HFCB Temp R1 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1_HI | °C | 133 | 1
| SVT EPICS HFCB Temp R1 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1_LO | °C | 134 | 2
| SVT EPICS HFCB Temp R2 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2_HI | °C | 135 | 3
| SVT EPICS HFCB Temp R2 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2_LO | °C | 136 | 4
| SVT EPICS HFCB Temp R3 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3_HI | °C | 137 | 5
| SVT EPICS HFCB Temp R3 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3_LO | °C | 138 | 6
| SVT EPICS Detector Int Temp R2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R2_HI | °C | 139 | 7
| SVT EPICS Detector Int Temp R2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R2_LO | °C | 140 | 8
| SVT EPICS Detector Int Temp R3 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R3_HI | °C | 141 | 9
| SVT EPICS Detector Int Temp R3 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R3_LO | °C | 142 | 10
| SVT EPICS Ambient Temp 1 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP1_HI | °C | 143 | 11
| SVT EPICS Ambient Temp 1 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP1_LO | °C | 144 | 12
| SVT EPICS Ambient Temp 2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP2_HI | °C | 145 | 13
| SVT EPICS Ambient Temp 2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP2_LO | °C | 146 | 14
| SVT EPICS Det Internal Humidity R2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R2_HI | %RH | 147 | 15
| SVT EPICS Det Internal Humidity R2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R2_LO | %RH | 148 | 16
| SVT EPICS Det Internal Humidity R3 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R3_HI | %RH | 149 | 17
| SVT EPICS Det Internal Humidity R3 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R3_LO | %RH | 150 | 18
| SVT EPICS Ambient Humidity H1 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID1_HI | %RH | 151 | 19
| SVT EPICS Ambient Humidity H1 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID1_LO | %RH | 152 | 20
| SVT EPICS Ambient Humidity H2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID2_HI | %RH | 153 | 21
| SVT EPICS Ambient Humidity H2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID2_LO | %RH | 154 | 22
| SVT EPICS Det Internal Dew Point R2 Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_DEWP_R2_THRES |  | 155 | 23
| SVT EPICS Det Internal Dew Point R3 Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_DEWP_R3_THRES |  | 156 | 24
| SVT EPICS Ambient Dew Point 1 Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_DEWP1_THRES |  | 157 | 25
| SVT EPICS Ambient Dew Point 2 Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_DEWP2_THRES |  | 158 | 26
| SVT EPICS Outlet Coolant Flow Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW_HI | L/Min | 159 | 27
| SVT EPICS Outlet Coolant Flow Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW_LO | L/Min | 160 | 28
| SVT EPICS Inlet Coolant Flow Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_IN_FLOW_HI | L/Min | 161 | 29
| SVT EPICS Inlet Coolant Flow Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_IN_FLOW_LO | L/Min | 162 | 30
| SVT EPICS Coolant Temp Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_TEMP_HI | °C | 163 | 31
| SVT EPICS Coolant Temp Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_TEMP_LO | °C | 164 | 32
Threshold Control Status | SVT EPICS Threshold Control | Read Only | Boolean | B_DET_SVT_INTLK_EPICS_THRESH_CTRL | N/A | 165 | 1
Hardware Interlock Status | SVT EPICS Chiller Enable Status | Read Only | Boolean | B_DET_SVT_INTLK_CHILLER_ENABLE_STAT | N/A | 166 | 1
| SVT EPICS Chiller Override Status | Read Only | Boolean | B_DET_SVT_INTLK_CHILLER_OVERRIDE_STAT | N/A | 167 | 2
| SVT EPICS Mpod Enable Status | Read Only | Boolean | B_DET_SVT_INTLK_MPOD_ENABLE_STAT | N/A | 168 | 3
| SVT EPICS Mpod Overide Status | Read Only | Boolean | B_DET_SVT_INTLK_MPOD_OVERRIDE_STAT | N/A | 169 | 5
Interlock System Status | SVT EPICS cRIO Heartbeat | Read Only | Boolean | B_HW_CRIO_SVT_HEARTBEAT | N/A | 170 | 1
| SVT EPICS cRIO CPU Usage | Read Only | Double | B_HW_CRIO_SVT_CPULOAD | % | 171 | 2
| SVT EPICS System Uptime | Read Only | Double | B_HW_CRIO_SVT_UPTIME | Sec | 172 | 3

## Interlock Levels
SVT Hardware Interlock System Threshold Levels
SVT Region | SVT Sector - Module | cRio Threshold Signal Name | cRio Module Type | cRio Slot # | cRio Channel | LabVIEW Threshold Category | Cat # Type Count | Threshold # | Data Type | Signal Type | Comments | Hardware Interlock System Trip Level. | EPICS Alarm (Trip) Level | EPICS Type
1 | 1 | HFCB_UT_R1_M1_T | NI 9239 ADC | 1 | AI0 | Low Temp | 0 | 0 | Double | HFCB Temperature (Under Temp) | Temp from HFCB R1 M1 Top side | ≤9°C | ≤10°C | LL-Major
2 | 1 | HFCB_UT_R2_M1_T | NI 9239 ADC | 1 | AI1 | Low Temp | 1 | 1 | Double | HFCB Temperature (Under Temp) | Temp from HFCB R2 M1 Top side | ≤9°C | ≤10°C | LL-Major
3 | 1 | HFCB_UT_R3_M1_T | NI 9239 ADC | 1 | AI2 | Low Temp | 2 | 2 | Double | HFCB Temperature (Under Temp) | Temp from HFCB R3 M1 Top side | ≤9°C | ≤10°C | LL-Major
4 | 1 | HFCB_UT_R4_M1_T | NI 9239 ADC | 1 | AI3 | Low Temp | 3 | 3 | Double | HFCB Temperature (Under Temp) | Temp from HFCB R4 M1 Top side | ≤9°C | ≤10°C | LL-Major
1 | 1 | HFCB_OT_R1_M1_T | NI 9239 ADC | 1 | AI0 | High Temp | 0 | 4 | Double | HFCB Temperature (Over Temp) | Temp from HFCB R1 M1 Top side | ≥34°C | ≥33°C | HH-Major
2 | 1 | HFCB_OT_R2_M1_T | NI 9239 ADC | 1 | AI1 | High Temp | 1 | 5 | Double | HFCB Temperature (Over Temp) | Temp from HFCB R2 M1 Top side | ≥34°C | ≥33°C | HH-Major
3 | 1 | HFCB_OT_R3_M1_T | NI 9239 ADC | 1 | AI2 | High Temp | 2 | 6 | Double | HFCB Temperature (Over Temp) | Temp from HFCB R3 M1 Top side | ≥34°C | ≥33°C | HH-Major
4 | 1 | HFCB_OT_R4_M1_T | NI 9239 ADC | 1 | AI3 | High Temp | 3 | 7 | Double | HFCB Temperature (Over Temp) | Temp from HFCB R4 M1 Top side | ≥34°C | ≥33°C | HH-Major
2 | N/A | Det_Int_UT_R2 | NI 9217 RTD | 3 | RTD0 | Low Temp | 4 | 8 | Double | Detector Internal Temperature (Under Temp) | Temp from R2 Support Ring - C Slot, SB10, ESC 3 | ≤11°C | ≤12°C | LL-Major
3 | N/A | Det_Int_UT_R3 | NI 9217 RTD | 3 | RTD1 | Low Temp | 5 | 9 | Double | Detector Internal Temperature (Under Temp) | Temp from R3 Support Ring - C Slot, SB12, ESC 6 | ≤11°C | ≤12°C | LL-Major
4 | 2 | Det_Int_UT_R4 | NI 9217 RTD | 3 | RTD2 | Low Temp | 6 | 10 | Double | Detector Internal Temperature (Under Temp) | Temp from R4 - M2, SB20 | ≤11°C | ≤12°C | LL-Major
2 | N/A | Det_Int_OT_R2 | NI 9217 RTD | 3 | RTD0 | High Temp | 4 | 11 | Double | Detector Internal Temperature (Over Temp) | Temp from R2 Support Ring - C Slot, SB10, ESC 3 | ≥31°C | ≥30°C | HH-Major
3 | N/A | Det_Int_OT_R3 | NI 9217 RTD | 3 | RTD1 | High Temp | 5 | 12 | Double | Detector Internal Temperature (Over Temp) | Temp from R3 Support Ring - C Slot, SB12, ESC 6 | ≥31°C | ≥30°C | HH-Major
4 | 2 | Det_Int_OT_R4 | NI 9217 RTD | 3 | RTD2 | High Temp | 6 | 13 | Double | Detector Internal Temperature (Over Temp) | Temp from R4 - M2, SB20 | ≥31°C | ≥30°C | HH-Major
N/A | N/A | Det_Amb_UT_T1 | NI 9217 RTD | 4 | RTD0 | Low Temp | 7 | 14 | Double | Ambient Temperature (Under Temp) | Temp from Ambient SB - sensor 1 | ≤11°C | ≤12°C | LL-Major
N/A | N/A | Det_Amb_UT_T2 | NI 9217 RTD | 4 | RTD1 | Low Temp | 8 | 15 | Double | Ambient Temperature (Under Temp) | Temp from Ambient SB - sensor 2 | ≤11°C | ≤12°C | LL-Major
N/A | N/A | Det_Amb_OT_T1 | NI 9217 RTD | 4 | RTD0 | High Temp | 7 | 16 | Double | Ambient Temperature (Over Temp) | Temp from Ambient SB - sensor 1 | ≥31°C | ≥30°C | HH-Major
N/A | N/A | Det_Amb_OT_T2 | NI 9217 RTD | 4 | RTD1 | High Temp | 8 | 17 | Double | Ambient Temperature (Over Temp) | Temp from Ambient SB - sensor 2 | ≥31°C | ≥30°C | HH-Major
2 | N/A | Det_Int_UH_R2 | NI 9205 ADC | 6 | AI0 | Low Humidity | 0 | 18 | Double | Detector Internal Humidity (Under Humidity) | Humidity from R2 Support Ring - C Slot, SB10, ESC 3 | ≤4% | ≤5% | LL-Major
3 | N/A | Det_Int_UH_R3 | NI 9205 ADC | 6 | AI1 | Low Humidity | 1 | 19 | Double | Detector Internal Humidity (Under Humidity) | Humidity from R3 Support Ring - C Slot, SB12, ESC 6 | ≤4% | ≤5% | LL-Major
4 | 2 | Det_Int_UH_R4 | NI 9205 ADC | 6 | AI2 | Low Humidity | 2 | 20 | Double | Detector Internal Humidity (Under Humidity) | Humidity from R4 - M2, SB20 | ≤4% | ≤5% | LL-Major
2 | N/A | Det_Int_OH_R2 | NI 9205 ADC | 6 | AI0 | High Humidity | 0 | 21 | Double | Detector Internal Humidity (Over Humidity) | Humidity from R2 Support Ring - C Slot, SB10, ESC 3 | ≥71% | ≥70% | HH-Major
3 | N/A | Det_Int_OH_R3 | NI 9205 ADC | 6 | AI1 | High Humidity | 1 | 22 | Double | Detector Internal Humidity (Over Humidity) | Humidity from R3 Support Ring - C Slot, SB12, ESC 6 | ≥71% | ≥70% | HH-Major
4 | 2 | Det_Int_OH_R4 | NI 9205 ADC | 6 | AI2 | High Humidity | 2 | 23 | Double | Detector Internal Humidity (Over Humidity) | Humidity from R4 - M2, SB20 | ≥71% | ≥70% | HH-Major
2 | N/A | Det_Int_DP_R2 | N/A | N/A | N/A | Dew Point | 0 | 24 | Double | Detector Internal Dew Point | Calculated from R2 temp, R2 Humidity | ≤2.5 | ≤3 | LL-Major
3 | N/A | Det_Int_DP_R3 | N/A | N/A | N/A | Dew Point | 1 | 25 | Double | Detector Internal Dew Point | Calculated from R3 temp, R3 Humidity | ≤2.5 | ≤3 | LL-Major
4 | 2 | Det_Int_DP_R4 | N/A | N/A | N/A | Dew Point | 2 | 26 | Double | Detector Internal Dew Point | Calculated from R4 temp, R4 Humidity | ≤2.5 | ≤3 | LL-Major
N/A | N/A | Det_Amb_UH_H1 | NI 9205 ADC | 6 | AI3 | Low Humidity | 3 | 27 | Double | Ambient Humidity (Under Humidity) | Humidity from Ambient SB - sensor 1 | ≤4% | ≤5% | LL-Major
N/A | N/A | Det_Amb_UH_H2 | NI 9205 ADC | 6 | AI4 | Low Humidity | 4 | 28 | Double | Ambient Humidity (Under Humidity) | Humidity from Ambient SB - sensor 2 | ≤4% | ≤5% | LL-Major
N/A | N/A | Det_Amb_OH_H1 | NI 9205 ADC | 6 | AI3 | High Humidity | 3 | 29 | Double | Ambient Humidity (Over Humidity) | Humidity from Ambient SB - sensor 1 | ≥71% | ≥70% | HH-Major
N/A | N/A | Det_Amb_OH_H2 | NI 9205 ADC | 6 | AI4 | High Humidity | 4 | 30 | Double | Ambient Humidity (Over Humidity) | Humidity from Ambient SB - sensor 2 | ≥71% | ≥70% | HH-Major
N/A | N/A | Det_Amb_DP_1 | N/A | N/A | N/A | Dew Point | 3 | 31 | Double | Ambient Dew Point | Calculated from Ambient temp 1, Ambient Humidity 1 | ≤3 | ≤3 | LL-Major
N/A | N/A | Det_Amb_DP_2 | N/A | N/A | N/A | Dew Point | 4 | 32 | Double | Ambient Dew Point | Calculated from Ambient temp 2, Ambient Humidity 2 | ≤3 | ≤3 | LL-Major
R1-R3 | N/A | Cool_U_flow_R1_R3 | NI 9239 ADC | 5 | AI0 | Under Flow | 0 | 33 | Double | Coolant Flow (Under Flow) | Coolant Flow for Region 1-3 | ≤.15 liters/min | ≤.25 liters/min | LL-Major
R1-R3 | N/A | Cool_O_flow_R1_R3 | NI 9239 ADC | 5 | AI0 | Over Flow | 1 | 34 | Double | Coolant Flow (Over Flow) | Coolant Flow for Region 1-3 | ≥10 liters/min | ≥9 liters/min | HH-Major
R4 | N/A | Cool_U_flow_R4 | NI 9239 ADC | 5 | AI1 | Under Flow | 0 | 35 | Double | Coolant Flow (Under Flow) | Coolant Flow for Region 4 | ≤.15 liters/min | ≤.25 liters/min | LL-Major
R4 | N/A | Cool_O_flow_R4 | NI 9239 ADC | 5 | AI1 | Over Flow | 1 | 36 | Double | Coolant Flow (Over Flow) | Coolant Flow for Region 4 | ≥10 liters/min | ≥9 liters/min | HU-Major
N/A | N/A | Cool_UT_1 | NI 9239 ADC | 5 | AI2 | Low Temp | 9 | 37 | Double | Coolant Temperature (Under Temp) | Coolant Temperature (Measured separately from chiller) | ≤9°C | ≤10°C | LL-Major
N/A | N/A | Cool_OT_1 | NI 9239 ADC | 5 | AI2 | High Temp | 9 | 38 | Double | Coolant Temperature (Over Temp) | Coolant Temperature (Measured separately from chiller) | ≥24°C | ≥23°C | HH-Major
N/A | N/A | Cool_Leak_1_ON | NI 9239 ADC | 5 | AI3 | Coolant Leak | 0 | 39 | Double | Coolant leak #1 is ON (Leak is detected) | Signal from Panasonic Leak controller (Y1) (24 V - ON) | ≥9.5 V | N/A | N/A
N/A | N/A | Cool_Leak_1_OFF | NI 9239 ADC | 5 | AI3 | Coolant Leak | 1 | 40 | Double | Coolant leak #1 is OFF | Signal from Panasonic Leak controller (Y1) (~.2V? - OFF) | ≤.2 V | N/A | N/A
N/A | N/A | +5V_Supply_UV | NI 9205 ADC | 6 | AI18 | +5V Supply | 0 | 42 | Double | +5V Power Supply (Under Voltage) | Internal supply for Mpod enables and humidity sensors | ≤4.5 V | N/A | N/A
N/A | N/A | +5V_Supply_OV | NI 9205 ADC | 6 | AI18 | +5V Supply | 0 | 43 | Double | +5V Power Supply (Over Voltage) | Internal supply for Mpod enables and humidity sensors | ≥5.5 V | N/A | N/A
N/A | N/A | Mpod_Crate_Override | NI 9205 ADC | 6 | AI19 | Override | 0 | 44 | Boolean | Override Mpod Crate disable is High is ON, Low is OFF | Disables Interlock system- Always powers Mpod crates | TBD | N/A | N/A
N/A | N/A | Chiller_Overide | NI 9205 ADC | 6 | AI20 | Override | 0 | 45 | Boolean | Override Chiller disable is High is ON, Low is OFF | Disables Interlock system- Always powers Chiller | TBD | N/A | N/A

## Signal Enables
SVT Hardware Interlock System Signal Enables
Enable # | SVT Region | SVT Sector - Module | cRio Module Type | cRio Slot # | cRio Channel | Data Type | Signal Type | Comments
0 | 1 | 1 | NI 9239 ADC | 1 | AI0 | Boolean | HFCB Temperature | Enables Alarm - Temp from HFCB R1 M1 Top side Sensor
1 | 2 | 1 | NI 9239 ADC | 1 | AI1 | Boolean | HFCB Temperature | Enables Alarm - Temp from HFCB R1 M1 Top side Sensor
2 | 3 | 1 | NI 9239 ADC | 1 | AI2 | Boolean | HFCB Temperature | Enables Alarm - Temp from HFCB R1 M1 Top side Sensor
3 | 4 | 1 | NI 9239 ADC | 1 | AI3 | Boolean | HFCB Temperature | Enables Alarm - Temp from HFCB R1 M1 Top side Sensor
4 | 2 | N/A | NI 9217 RTD | 3 | RTD0 | Boolean | Detector Internal Temperature | Enables Alarm - Temp from R2 Support Ring - C Slot, SB10, ESC 3
5 | 3 | N/A | NI 9217 RTD | 3 | RTD1 | Boolean | Detector Internal Temperature | Enables Alarm - Temp from R3 Support Ring - C Slot, SB12, ESC 6
6 | 4 | 2 | NI 9217 RTD | 3 | RTD2 | Boolean | Detector Internal Temperature | Enables Alarm - Temp from R4 - M2, SB20
7 | N/A | N/A | NI 9217 RTD | 4 | RTD0 | Boolean | Ambient Temperature | Enables Alarm - Temp from Ambient SB - sensor 1
8 | N/A | N/A | NI 9217 RTD | 4 | RTD1 | Boolean | Ambient Temperature | Enables Alarm - Temp from Ambient SB - sensor 2
9 | 2 | N/A | NI 9205 ADC | 6 | AI0 | Boolean | Detector Internal Humidity | Enables Alarm - Humidity from R2 Support Ring - C Slot, SB10, ESC 3
10 | 3 | N/A | NI 9205 ADC | 6 | AI1 | Boolean | Detector Internal Humidity | Enables Alarm - Humidity from R3 Support Ring - C Slot, SB12, ESC 6
11 | 4 | 2 | NI 9205 ADC | 6 | AI2 | Boolean | Detector Internal Humidity | Enables Alarm - Humidity from R4 - M2, SB20
12 | 2 | N/A | N/A | N/A | N/A | Boolean | Detector Internal Dew Point | Enables Alarm - Calculated from R2 temp, R2 Humidity
13 | 3 | N/A | N/A | N/A | N/A | Boolean | Detector Internal Dew Point | Enables Alarm - Calculated from R3 temp, R3 Humidity
14 | 4 | 2 | N/A | N/A | N/A | Boolean | Detector Internal Dew Point | Enables Alarm - Calculated from R4 temp, R4 Humidity
15 | N/A | N/A | NI 9205 ADC | 6 | AI3 | Boolean | Ambient Humidity | Enables Alarm - Humidity from Ambient SB - sensor 1
16 | N/A | N/A | NI 9205 ADC | 6 | AI4 | Boolean | Ambient Humidity | Enables Alarm - Humidity from Ambient SB - sensor 2
17 | N/A | N/A | N/A | N/A | N/A | Boolean | Ambient Dew Point | Enables Alarm - Calculated from Ambient temp 1, Ambient Humidity 1
18 | N/A | N/A | N/A | N/A | N/A | Boolean | Ambient Dew Point | Enables Alarm - Calculated from Ambient temp 2, Ambient Humidity 2
19 | R1-R3 | N/A | NI 9239 ADC | 5 | AI0 | Boolean | Coolant Flow | Enables Alarm - Coolant Flow for Region 1-3
20 | R4 | N/A | NI 9239 ADC | 5 | AI1 | Boolean | Coolant Flow | Enables Alarm - Coolant Flow for Region 4
21 | N/A | N/A | NI 9239 ADC | 5 | AI2 | Boolean | Coolant Temperature | Enables Alarm - Coolant Temperature (Measured separately from chiller)
22 | N/A | N/A | NI 9239 ADC | 5 | AI3 | Boolean | Coolant leak #1 | Enables Alarm - Signal from Panasonic Leak controller (Y1) (24 V - ON)

## Dewpoint Calculations
Magnus Formula |  |  | H = (log10(RH)-2)/0.4343 + (17.62*T)/(243.12+T);
Used in Hardware Interlock System |  |  | Dp = 243.12*H/(17.62-H); // this is the dew point in Celsius
T=Temperature in degrees C |  |  | Dp Alarm (EPICS) = T - DP
RH=Relative Humidity %
Input Numbers | [7 empty] | EPICS ALARM LIMITS
[7 empty] | L | 5 | Minor
| RH= | 33.69 | % | H= | 0.095185 |  | H | 0 | No Alarm
| Temp= | 17.5 | °C | DP = | 1.3205 |  | LL | 3 | Major
[7 empty] | HH | 0 | No Alarm
|  |  |  | Dewpoint alarm = | 16.1795 | The EPICS Alarm limits apply to THIS Number
Simple Formula |  |  | Dp = T -((100-RH)/5)
T=Temperature in degrees C |  |  | Dp Alarm (EPICS) = T - DP
RH=Relative Humidity %
Input Numbers
EPICS ALARM LIMITS
[7 empty] | L | 5 | Minor
| RH= | 33.69 | % |  |  |  | H | 0 | No Alarm
| Temp= | 17.5 | °C | DP = | 4.238 |  | LL | 3 | Major
[7 empty] | HH | 0 | No Alarm
|  |  |  | Dewpoint alarm = | 13.262 | The EPICS Alarm limits apply to THIS Number

## Mpod Crate Enable
Once enabled, the USB port is not used again for control or monitoring the Mpod crate.
When the CRATE_ENABLE signal is 0V, all channels of the Mpod crate will ramp down at their pre-programmed rate.
The SVT LV & HV modules do not respond identically to a crate disable event.
Both modules respond correctly by ramping down at their programmed rate at the removal of the CRATE_ENABLE signal however,
after the crate disable event, the LV modules automatically reset upon the return of the CRATE_ENABLE signal.
The HV modules do not automatically reset and require an EPICS hard reset to recover.