## cRio Module Assignments
FT Hardware Interlock System Channel Assignments
| Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
Channel | NI 9265 - 0-20mA output | Empty | NI 9216 RTD | Empty | NI 9401 - TTL DIO | NI 9205 ADC | Empty | NI 9485 Relay
Ch 0 | Calorimeter Chiller Interlock Interface |  | Calorimeter Temp 1 |  | Spare | Calorimeter Humidity 1 |  | CAEN Calorimeter HV Card 1 Enable
Ch 1 | Spare |  | Calorimeter Temp 2 |  | Spare | Calorimeter Humidity 2 |  | CAEN Calorimeter HV Card 2 Enable
Ch 2 | Spare |  | Calorimeter Temp 3 |  | Spare | Calorimeter Gas Flow |  | CAEN Calorimeter HV Card 3 Enable
Ch 3 | Spare |  | Calorimeter Temp 4 |  | Spare | Spare |  | CAEN Hodoscope HV Card 1 Enable
Ch 4 | Slot 3: Calorimeter Temp 5; Slot 5: Spare; Slot 6: Spare; Slot 8: CAEN Hodoscope HV Card 2 Enable
Ch 5 | Slot 3: Calorimeter Temp 6; Slot 5: Spare; Slot 6: Spare; Slot 8: CAEN Hodoscope HV Card 3 Enable
Ch 6 | Slot 3: Hodoscope Temp 1; Slot 5: Spare; Slot 6: Spare; Slot 8: Mpod LV Calorimeter Enable
Ch 7 | Slot 3: Hodoscope Temp 2; Slot 5: Spare; Slot 6: Spare; Slot 8: Mpod LV Hodoscope Enable
Ch 8 | Slot 6: Spare (CH16)
Ch 9 | Slot 6: Spare (CH17)
Ch 10 | Slot 6: +5V Supply Monitor (Ch18)
Ch 11 | Slot 6: Spare (CH19)
Ch 12 | Slot 6: Spare (CH20)
Ch 13 | Slot 6: Spare (CH21)
Ch 14 | [5 empty] | Spare (CH22) |  |  | NI 9035 Controller |  | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
Ch 15 | [5 empty] | Spare (CH23) |  |  |  |  | NI 9265 | Empty | NI 9216 | Empty | NI 9401 | NI 9205 | Empty | NI 9485
Comments
| Requires External power supply |  |  |  | CH 0-3 (port 1) Inputs | Humidity sensors powered
| Can use +24V fused to module |  |  |  | CH 4-7 (port 2) Outputs | by +5V supply (Fused)
| Pin 8 = +24V , Pin 9 = Gnd | [9 empty] | Slot 1: cRio Module Description
NI 9265 (4) channels, 0 to 20 mA, 16-Bit, 100 kS/s, Analog Output Module
NI 9216 (8) Channels, RTD module, PT100 RTD, 24-Bit, 50S/S/CH, Analog Input Module
NI 9401 (8) Channels, 100 ns, TTL Digital Input/Output Module
| Signal Name | Number of Channels | Input / Output | NI Module | Description | [5 empty] | Slot 1: NI 9205 (16) Differential Channels, +/- 200mV to +/- 10V, 16 bit resolution
| Calorimeter Temperature | 6 | RTD Inputs | NI 9216 | For PT100 RTD's | [5 empty] | Slot 1: NI 9485 (8) Channels, Solid State Relay module, 60VDC, 750 mA, isolated channels
| Hodoscope Temperature | 2 | RTD Inputs | NI 9216 | For PT100 RTD's
| Calorimeter Humidity | 2 | Analog Voltage Inputs | NI 9205 | Humidity sensors are powered by Rhino PSP05-DC24-5 (+5 DIN Rail Power supply)
| Chiller Interlock | 1 | Analog Current Outputs | NI 9265 | 0-20 mA interface to the Lauda chiller LRZ 912 analog input module (Pump Power) | [5 empty] | Slot 1: Notes
| HV Interlock | 7 | Relay | NI 9485 | Each HV module is interlocked individually |  |  |  |  | Interlocked HV | Slot 1: CAEN HV boards- 3X 1530P for Calorimeter (Has lemo for interlock)
| LV Interlock | 2 | Relay | NI 9485 | Each LV module is interlocked individually |  |  |  |  | Interlocked HV | Slot 1: CAEN HV boards- 3X A1737P for Hodoscope (Has lemo for interlock)
| Calorimeter Gas Flow | 1 | Analog Input | NI 9205 | 0-5V signal from flow Meter, Power to meter is Fused +24V from chassis power supply |  |  |  |  | Chiller Interlock | Slot 1: Lauda Chiller (4-20 mA interface) is used for Calorimeter
| +5V supply Monitor | 1 | Analog Input | NI 9205 | Checks +5V supply used for humidity sensors and Mpod crate enable |  |  |  |  | Ramp Sequence | Slot 1: Ramp down sequence -HV then LV for both detectors ~ 1 sec wait
[10 empty] | Temp Limits | Slot 1: Calorimeter Temp limits - 40C warning / 50C trip
[10 empty] | RTD Type | Slot 1: 4 - wire RTD's are used - Already installed by FT Group
[10 empty] | Interlocked LV | Slot 1: (2) Mpod LV boards - individually interlocked (1) Calorimeter (1) Hodoscope; Slot 8: Calorimeter uses 4 LV channels (+5v) 5 Amp Limit
[10 empty] | Gas Flow | Slot 1: Gas flow (N2) is monitored for Calorimeter (24V from cRio supply)

## Signal Enables
FT Hardware Interlock System Signal Enables
Enable # | FT Detector | cRio Module Type | cRio Slot # | cRio Channel | Data Type | Signal Type | Comments
0 | Calorimeter | NI 9216 RTD | 3 | RTD0 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 1) from Calorimeter
1 | Calorimeter | NI 9216 RTD | 3 | RTD1 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 2) from Calorimeter
2 | Calorimeter | NI 9216 RTD | 3 | RTD2 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 3) from Calorimeter
3 | Calorimeter | NI 9216 RTD | 3 | RTD3 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 4) from Calorimeter
4 | Calorimeter | NI 9216 RTD | 3 | RTD4 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 5) from Calorimeter
5 | Calorimeter | NI 9216 RTD | 3 | RTD5 | Boolean | Calorimeter Temperature | Enables Alarm - Temperature (Sensor 6) from Calorimeter
6 | Calorimeter | NI 9205 ADC | 6 | AI0 | Boolean | Calorimeter Humidity | Enables Alarm - Humidity (Sensor 1) from Calorimeter
7 | Calorimeter | NI 9205 ADC | 6 | AI1 | Boolean | Calorimeter Humidity | Enables Alarm - Humidity (Sensor 2) from Calorimeter
8 | Calorimeter | NI 9205 ADC | 6 | AI2 | Boolean | Calorimeter Gas Flow | Enables Alarm - Calorimeter N2 Gas Flow
9 | Hodoscope | NI 9216 RTD | 3 | RTD6 | Boolean | Hodoscope Temperature | Enables Alarm - Temperature (Sensor 1) from Hodoscope
10 | Hodoscope | NI 9216 RTD | 3 | RTD7 | Boolean | Hodoscope Temperature | Enables Alarm - Temperature (Sensor 2) from Hodoscope

## Interlock Levels
FT Hardware Interlock System Threshold Levels
FT Detector | cRio Threshold Signal Name | cRio Module Type | cRio Slot # | cRio Channel | LabVIEW Threshold Category | Cat # Type Count | Threshold # | Data Type | Signal Type | Comments | Hardware Interlock System Trip Level.
Calorimeter | FT_Cal_UT_T1 | NI 9216 RTD | 3 | RTD0 | Low Temp | 0 | 0 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 1) Temperature | ≤X°C
Calorimeter | FT_Cal_UT_T2 | NI 9216 RTD | 3 | RTD1 | Low Temp | 1 | 1 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 2) Temperature | ≤X°C
Calorimeter | FT_Cal_UT_T3 | NI 9216 RTD | 3 | RTD2 | Low Temp | 2 | 2 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 3) Temperature | ≤X°C
Calorimeter | FT_Cal_UT_T4 | NI 9216 RTD | 3 | RTD3 | Low Temp | 3 | 3 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 4) Temperature | ≤X°C
Calorimeter | FT_Cal_UT_T5 | NI 9216 RTD | 3 | RTD4 | Low Temp | 4 | 4 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 5) Temperature | ≤X°C
Calorimeter | FT_Cal_UT_T6 | NI 9216 RTD | 3 | RTD5 | Low Temp | 5 | 5 | Double | Calorimeter Temperature (Under Temp) | Calorimeter (Sensor 6) Temperature | ≤X°C
Calorimeter | FT_Cal_OT_T1 | NI 9216 RTD | 3 | RTD0 | HIgh Temp | 0 | 6 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 1) Temperature | ≥50°C
Calorimeter | FT_Cal_OT_T2 | NI 9216 RTD | 3 | RTD1 | HIgh Temp | 1 | 7 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 2) Temperature | ≥50°C
Calorimeter | FT_Cal_OT_T3 | NI 9216 RTD | 3 | RTD2 | HIgh Temp | 2 | 8 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 3) Temperature | ≥50°C
Calorimeter | FT_Cal_OT_T4 | NI 9216 RTD | 3 | RTD3 | HIgh Temp | 3 | 9 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 4) Temperature | ≥50°C
Calorimeter | FT_Cal_OT_T5 | NI 9216 RTD | 3 | RTD4 | HIgh Temp | 4 | 10 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 5) Temperature | ≥50°C
Calorimeter | FT_Cal_OT_T6 | NI 9216 RTD | 3 | RTD5 | HIgh Temp | 5 | 11 | Double | Calorimeter Temperature (Over Temp) | Calorimeter (Sensor 6) Temperature | ≥50°C
Hodoscope | FT_Hod_UT_T1 | NI 9216 RTD | 3 | RTD6 | Low Temp | 0 | 12 | Double | Hodoscope Temperature (Under Temp) | Hodoscope (Sensor 1) Temperature | ≤X°C
Hodoscope | FT_Hodl_UT_T2 | NI 9216 RTD | 3 | RTD7 | Low Temp | 1 | 13 | Double | Hodoscope Temperature (Under Temp) | Hodoscope (Sensor 2) Temperature | ≤X°C
Hodoscope | FT_Hod_OT_T1 | NI 9216 RTD | 3 | RTD6 | HIgh Temp | 0 | 14 | Double | Hodoscope Temperature (Under Temp) | Hodoscope (Sensor 1) Temperature | ≥X°C
Hodoscope | FT_Hod_OT_T2 | NI 9216 RTD | 3 | RTD7 | HIgh Temp | 1 | 15 | Double | Hodoscope Temperature (Under Temp) | Hodoscope (Sensor 2) Temperature | ≥X°C
Calorimeter | FT_Cal_UH_H1 | NI 9205 ADC | 6 | AI0 | Low Humidity | 0 | 16 | Double | Calorimeter Humidity (Under Humidity) | Calorimeter (Sensor 1) Humidity | ≤X%
Calorimeter | FT_Cal_UH_H2 | NI 9205 ADC | 6 | AI1 | Low Humidity | 1 | 17 | Double | Calorimeter Humidity (Under Humidity) | Calorimeter (Sensor 2) Humidity | ≤X%
Calorimeter | FT_Cal_OH_H1 | NI 9205 ADC | 6 | AI0 | High Humidity | 0 | 18 | Double | Calorimeter Humidity (Over Humidity) | Calorimeter (Sensor 1) Humidity | ≥X%
Calorimeter | FT_Cal_OH_H2 | NI 9205 ADC | 6 | AI1 | High Humidity | 1 | 19 | Double | Calorimeter Humidity (Over Humidity) | Calorimeter (Sensor 2) Humidity | ≥X%
Calorimeter | FT_Cal_UF_F1 | NI 9205 ADC | 6 | AI2 | Under Flow | 0 | 20 | Double | Calorimeter Gas Flow (Under Flow) |  | ≤ X sccm/min
Calorimeter | FT_Cal_OV_F1 | NI 9205 ADC | 6 | AI2 | Over Flow | 1 | 21 | Double | Calorimeter Gas Flow (Over Flow) |  | ≥X sccm/min
N/A | +5V_Supply_UV | NI 9205 ADC | 6 | AI18 | +5V Supply | 0 | 22 | Double | +5V Power Supply (Under Voltage) | Internal supply for Mpod enables and humidity sensors | ≤4.5 V
N/A | +5V_Supply_OV | NI 9205 ADC | 6 | AI18 | +5V Supply | 1 | 23 | Double | +5V Power Supply (Over Voltage) | Internal supply for Mpod enables and humidity sensors | ≥5.5 V
N/A | Mpod_Module_Override | NI 9205 ADC | 6 | AI19 | Override | 0 |  | Boolean | Override Mpod module disable is High is ON, Low is OFF | Disables Interlock system- Always powers Mpod modules | TBD
N/A | CAEN_HV_Overide | NI 9205 ADC | 6 | AI20 | Override | 0 |  | Boolean | Override HV disable is High is ON, Low is OFF | Disables Interlock system- Always powers CAEN HV | TBD

## EPICS Interface
Hall B FT Hardware Interlock System EPICS Interface
Signal Category | LabVIEW Signal Name | Access Type | Data Type | EPICS Process Variable (PV) | Units | PV # | Group #
Signal Monitoring | FT EPICS Calorimeter Temp #1 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_1 | °C | 1 | 1 | B_DET_FTC_INTLK_TEMP1
| FT EPICS Calorimeter Temp #2 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_2 | °C | 2 | 2 | B_DET_FTC_INTLK_TEMP2
| FT EPICS Calorimeter Temp #3 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_3 | °C | 3 | 3 | B_DET_FTC_INTLK_TEMP3
| FT EPICS Calorimeter Temp #4 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_4 | °C | 4 | 4 | B_DET_FTC_INTLK_TEMP4
| FT EPICS Calorimeter Temp #5 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_5 | °C | 5 | 5 | B_DET_FTC_INTLK_TEMP5
| FT EPICS Calorimeter Temp #6 | Read Only | Double | B_FT_INTERLOCKS_CAL_TEMP_6 | °C | 6 | 6 | B_DET_FTC_INTLK_TEMP6
| FT EPICS Hodoscope Temp #1 | Read Only | Double | B_FT_INTERLOCKS_HODO_TEMP_1 | °C | 7 | 7 | B_DET_FTH_INTLK_TEMP1
| FT EPICS Hodoscope Temp #2 | Read Only | Double | B_FT_INTERLOCKS_HODO_TEMP_2 | °C | 8 | 8 | B_DET_FTH_INTLK_TEMP2
| FT EPICS Calorimeter Humidity #1 | Read Only | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1 | %RH | 9 | 9 | B_DET_FTC_INTLK_HUMID1
| FT EPICS Calorimeter Humidity #2 | Read Only | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2 | %RH | 10 | 10 | B_DET_FTC_INTLK_HUMID2
| FT EPICS Calorimeter Gas Flow | Read Only | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW | sccm | 11 | 11 | B_DET_FTC_INTLK_FLOW
Individual Sensor Interlock Status | FT EPICS Cal Temp 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_HI_STATUS | N/A | 12 | 1 | B_DET_FTC_INTLK_TEMP1_HI_STAT
| FT EPICS Cal Temp 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LO_STATUS | N/A | 13 | 2 | B_DET_FTC_INTLK_TEMP1_LO_STAT
| FT EPICS Cal Temp 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_HI_STATUS | N/A | 14 | 3 | B_DET_FTC_INTLK_TEMP2_HI_STAT
| FT EPICS Cal Temp 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LO_STATUS | N/A | 15 | 4 | B_DET_FTC_INTLK_TEMP2_LO_STAT
| FT EPICS Cal Temp 3 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_HI_STATUS | N/A | 16 | 5 | B_DET_FTC_INTLK_TEMP3_HI_STAT
| FT EPICS Cal Temp 3 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LO_STATUS | N/A | 17 | 6 | B_DET_FTC_INTLK_TEMP3_LO_STAT
| FT EPICS Cal Temp 4 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_HI_STATUS | N/A | 18 | 7 | B_DET_FTC_INTLK_TEMP4_HI_STAT
| FT EPICS Cal Temp 4 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LO_STATUS | N/A | 19 | 8 | B_DET_FTC_INTLK_TEMP4_LO_STAT
| FT EPICS Cal Temp 5 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_HI_STATUS | N/A | 20 | 9 | B_DET_FTC_INTLK_TEMP5_HI_STAT
| FT EPICS Cal Temp 5 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LO_STATUS | N/A | 21 | 10 | B_DET_FTC_INTLK_TEMP5_LO_STAT
| FT EPICS Cal Temp 6 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_HI_STATUS | N/A | 22 | 11 | B_DET_FTC_INTLK_TEMP6_HI_STAT
| FT EPICS Cal Temp 6 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LO_STATUS | N/A | 23 | 12 | B_DET_FTC_INTLK_TEMP6_LO_STAT
| FT EPICS Hodo Temp 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_HI_STATUS | N/A | 24 | 13 | B_DET_FTH_INTLK_TEMP1_HI_STAT
| FT EPICS Hodo Temp 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LO_STATUS | N/A | 25 | 14 | B_DET_FTH_INTLK_TEMP1_LO_STAT
| FT EPICS Hodo Temp 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_HI_STATUS | N/A | 26 | 15 | B_DET_FTH_INTLK_TEMP2_HI_STAT
| FT EPICS Hodo Temp 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LO_STATUS | N/A | 27 | 16 | B_DET_FTH_INTLK_TEMP2_LO_STAT
| FT EPICS Cal Humidity 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_HI_STATUS | N/A | 28 | 17 | B_DET_FTC_INTLK_HUMID1_HI_STAT
| FT EPICS Cal Humidity 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LO_STATUS | N/A | 29 | 18 | B_DET_FTC_INTLK_HUMID1_LO_STAT
| FT EPICS Cal Humidity 2 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_HI_STATUS | N/A | 30 | 19 | B_DET_FTC_INTLK_HUMID2_HI_STAT
| FT EPICS Cal Humidity 2 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LO_STATUS | N/A | 31 | 20 | B_DET_FTC_INTLK_HUMID2_LO_STAT
| FT EPICS Cal Gas Flow 1 Hi Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_HI_STATUS | N/A | 32 | 21 | B_DET_FTC_INTLK_FLOW_HI_STAT
| FT EPICS Cal Gas Flow 1 Lo Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LO_STATUS | N/A | 33 | 22 | B_DET_FTC_INTLK_FLOW_LO_STAT
Sum of Calorimeter Interlocks Status | FT EPICS Any Calorimeter Interlocks Over Limit? | Read Only | Boolean | B_FT_INTERLOCKS_ANY_CALORIMETER_INTERLOCKS_OVER_LIMIT | N/A | 34 | 1 | B_DET_FTC_INTLK_ANY_OVERLIMIT
Sum of Calorimeter Temperature Status | FT EPICS Calorimeter Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_TEMPERATURE_STATUS | N/A | 35 | 1 | B_DET_FTC_INTLK_TEMP_STATUS
Sum of Calorimeter Humidity Status | FT EPICS Calorimeter Humidity Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_HUMIDITY_STATUS | N/A | 36 | 1 | B_DET_FTC_INTLK_HUMID_STATUS
Sum of Calorimeter Gas Flow Status | FT EPICS Calorimeter Gas Flow Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_GAS_FLOW_STATUS | N/A | 37 | 1 | B_DET_FTC_INTLK_FLOW_STATUS
Sum of Hodoscope Interlocks Status | FT EPICS Any Hodoscope Interlocks Over Limit? | Read Only | Boolean | B_FT_INTERLOCKS_ANY_HODOSCOPE_INTERLOCKS_OVER_LIMIT | N/A | 38 | 1 | B_DET_FTH_INTLK_ANY_OVERLIMIT
Sum of Hodoscope Temperature Status | FT EPICS Hodoscope Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_TEMPERATURE_STATUS | N/A | 39 | 1 | B_DET_FTH_INTLK_TEMP_STATUS
Individual Sensor Latched Errors | FT EPICS Cal Temp 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LATCHED_HI_ERROR | N/A | 40 | 1 | B_DET_FTC_INTLK_TEMP1_LATCHED_HI_ERR
| FT EPICS Cal Temp 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_LATCHED_LO_ERROR | N/A | 41 | 2 | B_DET_FTC_INTLK_TEMP1_LATCHED_LO_ERR
| FT EPICS Cal Temp 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LATCHED_HI_ERROR | N/A | 42 | 3 | B_DET_FTC_INTLK_TEMP2_LATCHED_HI_ERR
| FT EPICS Cal Temp 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_LATCHED_LO_ERROR | N/A | 43 | 4 | B_DET_FTC_INTLK_TEMP2_LATCHED_LO_ERR
| FT EPICS Cal Temp 3 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LATCHED_HI_ERROR | N/A | 44 | 5 | B_DET_FTC_INTLK_TEMP3_LATCHED_HI_ERR
| FT EPICS Cal Temp 3 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_LATCHED_LO_ERROR | N/A | 45 | 6 | B_DET_FTC_INTLK_TEMP3_LATCHED_LO_ERR
| FT EPICS Cal Temp 4 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LATCHED_HI_ERROR | N/A | 46 | 7 | B_DET_FTC_INTLK_TEMP4_LATCHED_HI_ERR
| FT EPICS Cal Temp 4 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_LATCHED_LO_ERROR | N/A | 47 | 8 | B_DET_FTC_INTLK_TEMP4_LATCHED_LO_ERR
| FT EPICS Cal Temp 5 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LATCHED_HI_ERROR | N/A | 48 | 9 | B_DET_FTC_INTLK_TEMP5_LATCHED_HI_ERR
| FT EPICS Cal Temp 5 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_LATCHED_LO_ERROR | N/A | 49 | 10 | B_DET_FTC_INTLK_TEMP5_LATCHED_LO_ERR
| FT EPICS Cal Temp 6 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LATCHED_HI_ERROR | N/A | 50 | 11 | B_DET_FTC_INTLK_TEMP6_LATCHED_HI_ERR
| FT EPICS Cal Temp 6 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_LATCHED_LO_ERROR | N/A | 51 | 12 | B_DET_FTC_INTLK_TEMP6_LATCHED_LO_ERR
| FT EPICS Hodo Temp 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LATCHED_HI_ERROR | N/A | 52 | 13 | B_DET_FTH_INTLK_TEMP1_LATCHED_HI_ERR
| FT EPICS Hodo Temp 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_LATCHED_LO_ERROR | N/A | 53 | 14 | B_DET_FTH_INTLK_TEMP1_LATCHED_LO_ERR
| FT EPICS Hodo Temp 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LATCHED_HI_ERROR | N/A | 54 | 15 | B_DET_FTH_INTLK_TEMP2_LATCHED_HI_ERR
| FT EPICS Hodo Temp 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_LATCHED_LO_ERROR | N/A | 55 | 16 | B_DET_FTH_INTLK_TEMP2_LATCHED_LO_ERR
| FT EPICS Cal Humidity 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LATCHED_HI_ERROR | N/A | 56 | 17 | B_DET_FTC_INTLK_HUMID1_LATCHED_HI_ERR
| FT EPICS Cal Humidity 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LATCHED_LO_ERROR | N/A | 57 | 18 | B_DET_FTC_INTLK_HUMID1_LATCHED_LO_ERR
| FT EPICS Cal Humidity 2 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LATCHED_HI_ERROR | N/A | 58 | 19 | B_DET_FTC_INTLK_HUMID1_LATCHED_HI_ERR
| FT EPICS Cal Humidity 2 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LATCHED_LO_ERROR | N/A | 59 | 20 | B_DET_FTC_INTLK_HUMID1_LATCHED_LO_ERR
| FT EPICS Cal Gas Flow 1 Latched Hi Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_HI_ERROR | N/A | 60 | 21 | B_DET_FTC_INTLK_FLOW_LATCHED_HI_ERR
| FT EPICS Cal Gas Flow 1 Latched Lo Error | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_LO_ERROR | N/A | 61 | 22 | B_DET_FTC_INTLK_FLOW_LATCHED_LO_ERR
Sum of Calorimeter Temperature Latched Errors | FT EPICS Calorimeter Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_TEMPERATURE_LATCHED_ERROR | N/A | 62 | 1 | B_DET_FTC_INTLK_TEMP_LATCHED_ERR
Sum of Calorimeter Humidity Latched Errors | FT EPICS Calorimeter Humidity Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_LATCHED_ERROR | N/A | 63 | 1 | B_DET_FTC_INTLK_HUMID_LATCHED_ERR
Sum of Calorimeter Gas Flow Latched Errors | FT EPICS Calorimeter Gas Flow Status | Read Only | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_LATCHED_ERROR | N/A | 64 | 1 | B_DET_FTC_INTLK_FLOW_LATCHED_ERR
Sum of Hodoscope Temperature Latched Errors | FT EPICS Hodoscope Temperature Status | Read Only | Boolean | B_FT_INTERLOCKS_HODO_TEMPERATURE_LATCHED_ERROR | N/A | 65 | 1 | B_DET_FTH_TEMP_LATCHED_ERR
Reset of All Latched Errors | FT EPICS Reset Latched Errors | Read/Write | Boolean | B_FT_INTERLOCKS_RESET_LATCHED_ERRORS | N/A | 66 | 1 | B_DET_FT_INTLK_RESET_LATCHED_ERR
Individual Sensor Interlock Enables | FT EPICS Calorimeter Temp #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_1_INTERLOCK_ENABLE | N/A | 67 | 1 | B_DET_FTC_INTLK_TEMP1_ENABLE
| FT EPICS Calorimeter Temp #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_2_INTERLOCK_ENABLE | N/A | 68 | 2 | B_DET_FTC_INTLK_TEMP2_ENABLE
| FT EPICS Calorimeter Temp #3 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_3_INTERLOCK_ENABLE | N/A | 69 | 3 | B_DET_FTC_INTLK_TEMP3_ENABLE
| FT EPICS Calorimeter Temp #4 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_4_INTERLOCK_ENABLE | N/A | 70 | 4 | B_DET_FTC_INTLK_TEMP4_ENABLE
| FT EPICS Calorimeter Temp #5 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_5_INTERLOCK_ENABLE | N/A | 71 | 5 | B_DET_FTC_INTLK_TEMP5_ENABLE
| FT EPICS Calorimeter Temp #6 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_TEMP_6_INTERLOCK_ENABLE | N/A | 72 | 6 | B_DET_FTC_INTLK_TEMP5_ENABLE
| FT EPICS Hodoscope Temp #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_HODO_TEMP_1_INTERLOCK_ENABLE | N/A | 73 | 7 | B_DET_FTH_INTLK_TEMP1_ENABLE
| FT EPICS Hodoscope Temp #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_HODO_TEMP_2_INTERLOCK_ENABLE | N/A | 74 | 8 | B_DET_FTH_INTLK_TEMP1_ENABLE
| FT EPICS Calorimeter Humidity #1 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_1_INTERLOCK_ENABLE | N/A | 75 | 9 | B_DET_FTC_INTLK_HUMID1_ENABLE
| FT EPICS Calorimeter Humidity #2 Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_HUMIDITY_2_INTERLOCK_ENABLE | N/A | 76 | 10 | B_DET_FTC_INTLK_HUMID2_ENABLE
| FT EPICS Calorimeter Gas Flow Interlock Enable | Read/Write | Boolean | B_FT_INTERLOCKS_CAL_GAS_FLOW_INTERLOCK_ENABLE | N/A | 77 | 11 | B_DET_FTC_INTLK_FLOW_ENABLE
Individual Sensor Threshold Controls | FT EPICS Calorimeter Temp #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_1_HI_THRES | °C | 78 | 1 | B_DET_FTC_TEMP1_HI
| FT EPICS Calorimeter Temp #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_1_LO_THRES | °C | 79 | 2 | B_DET_FTC_TEMP1_LO
| FT EPICS Calorimeter Temp #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_2_HI_THRES | °C | 80 | 3 | B_DET_FTC_TEMP2_HI
| FT EPICS Calorimeter Temp #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_2_LO_THRES | °C | 81 | 4 | B_DET_FTC_TEMP2_LO
| FT EPICS Calorimeter Temp #3 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_3_HI_THRES | °C | 82 | 5 | B_DET_FTC_TEMP3_HI
| FT EPICS Calorimeter Temp #3 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_3_LO_THRES | °C | 83 | 6 | B_DET_FTC_TEMP3_LO
| FT EPICS Calorimeter Temp #4 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_4_HI_THRES | °C | 84 | 7 | B_DET_FTC_TEMP4_HI
| FT EPICS Calorimeter Temp #4 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_4_LO_THRES | °C | 85 | 8 | B_DET_FTC_TEMP4_LO
| FT EPICS Calorimeter Temp #5 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_5_HI_THRES | °C | 86 | 9 | B_DET_FTC_TEMP5_HI
| FT EPICS Calorimeter Temp #5 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_5_LO_THRES | °C | 87 | 10 | B_DET_FTC_TEMP5_LO
| FT EPICS Calorimeter Temp #6 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_6_HI_THRES | °C | 88 | 11 | B_DET_FTC_TEMP6_HI
| FT EPICS Calorimeter Temp #6 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_TEMP_6_LO_THRES | °C | 89 | 12 | B_DET_FTC_TEMP6_LO
| FT EPICS Hodoscope Temp #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_1_HI_THRES | °C | 90 | 13 | B_DET_FTH_TEMP1_HI
| FT EPICS Hodoscope Temp #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_1_LO_THRES | °C | 91 | 14 | B_DET_FTH_TEMP1_LO
| FT EPICS Hodoscope Temp #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_2_HI_THRES | °C | 92 | 15 | B_DET_FTH_TEMP2_HI
| FT EPICS Hodoscope Temp #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_HODO_TEMP_2_LO_THRES | °C | 93 | 16 | B_DET_FTH_TEMP1_LO
| FT EPICS Calorimeter Humidity #1 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1_HI_THRES | %RH | 94 | 17 | B_DET_FTC_HUMID1_HI
| FT EPICS Calorimeter Humidity #1 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_1_LO_THRES | %RH | 95 | 18 | B_DET_FTC_HUMID1_LO
| FT EPICS Calorimeter Humidity #2 Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2_HI_THRES | %RH | 96 | 19 | B_DET_FTC_HUMID2_HI
| FT EPICS Calorimeter Humidity #2 Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_HUMIDITY_2_LO_THRES | %RH | 97 | 20 | B_DET_FTC_HUMID2_LO
| FT EPICS Calorimeter Gas Flow Hi Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW_HI_THRES | sccm | 98 | 21 | B_DET_FTC_FLOW_HI
| FT EPICS Calorimeter Gas Flow Lo Threshold | Read/Write | Double | B_FT_INTERLOCKS_CAL_GAS_FLOW_LO_THRES | sccm | 99 | 22 | B_DET_FTC_FLOW_LO
Threshold Control Status | FT EPICS Threshold Control | Read Only | Boolean | B_FT_INTERLOCKS_EPICS_THRESHOLD_CONTROL | N/A | 100 | 1 | B_DET_FT_INTLK_EPICS_THRESH_CTRL
Hardware Interlock Status | FT EPICS Calorimeter LV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_LV_ENABLE_STATUS | N/A | 101 | 1 | B_DET_FTC_INTLK_LV_ENABLE_STAT
| FT EPICS Calorimeter HV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_HV_ENABLE_STATUS | N/A | 102 | 2 | B_DET_FTC_INTLK_HV_ENABLE_STAT
| FT EPICS Calorimeter Chiller Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_CALORIMETER_CHILLER_ENABLE_STATUS | N/A | 103 | 3 | B_DET_FTC_INTLK_CHILLER_ENABLE_STAT
| FT EPICS Hodoscope LV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_LV_ENABLE_STATUS | N/A | 104 | 4 | B_DET_FTH_INTLK_LV_ENABLE_STAT
| FT EPICS Hodoscope HV Enable Status | Read Only | Boolean | B_FT_INTERLOCKS_HODOSCOPE_HV_ENABLE_STATUS | N/A | 105 | 5 | B_DET_FTH_INTLK_HV_ENABLE_STAT
Interlock System Status | FT EPICS cRio Heartbeat | Read Only | Boolean | B_FT_INTERLOCKS_CRIO_HEARTBEAT | N/A | 106 | 1 | B_HW_CRIO_FT_HEARTBEAT
| FT EPICS cRio CPU Usage | Read Only | Double | B_FT_INTERLOCKS_CRIO_CPU_USEAGE | % | 107 | 2 | B_HW_CRIO_FT_CPULOAD
| FT EPICS System Uptime | Read Only | Double | B_FT_INTERLOCKS_SYSTEM_UPTIME | Sec | 108 | 3 | B_HW_CRIO_FT_UPTIME

## NI Signals
FT Hardware Interlock Signals by cRio Channels
2016-11-29
Category | FT Detector | NI cRio Module Type | cRio Slot # | cRio Channel + | cRio Connector Pin Name | cRio Connector Pin # | Hardware Interlock Cable ID | Interlock System Cable Asssembly Type | EPICS Main Control System Signal Name | Comments
Chiller Enable | Calorimeter | NI 9265 0-20mA | 1 | 0 | Aoo | 0 |  |  | B_FT_ | Chiller Pump Enable
Chiller Enable | Calorimeter | NI 9265 0-20mA | 1 | 0 | COM0 | 1
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 0 | EX0+ | 2 |  |  | B_FT_ | Calorimeter (Sensor 1) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 0 | RTD0+ | 3
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 0 | RTD0- | 4
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 0 | COM | 5
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 1 | EX1+ | 6 |  |  | B_FT_ | Calorimeter (Sensor 2) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 1 | RTD1+ | 7
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 1 | RTD1- | 8
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 1 | COM | 9
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 2 | EX2+ | 10 |  |  | B_FT_ | Calorimeter (Sensor 3) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 2 | RTD2+ | 11
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 2 | RTD2- | 12
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 2 | COM | 13
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 3 | EX3+ | 14 |  |  | B_FT_ | Calorimeter (Sensor 4) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 3 | RTD3+ | 15
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 3 | RTD3- | 16
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 3 | COM | 17
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 4 | EX4+ | 20 |  |  | B_FT_ | Calorimeter (Sensor 5) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 4 | RTD4+ | 21
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 4 | RTD4- | 22
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 4 | COM | 23
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 5 | EX5+ | 24 |  |  | B_FT_ | Calorimeter (Sensor 6) Temperature
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 5 | RTD5+ | 25
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 5 | RTD5- | 26
RTD Temp | Calorimeter | NI 9216 RTD | 3 | 5 | COM | 27
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 6 | EX6+ | 28 |  |  | B_FT_ | Hodoscope (Sensor 1) Temperature
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 6 | RTD6+ | 29
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 6 | RTD6- | 30
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 6 | COM | 31
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 7 | EX7+ | 32 |  |  | B_FT_ | Hodoscope (Sensor 2) Temperature
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 7 | RTD7+ | 33
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 7 | RTD7- | 34
RTD Temp | Hodoscope | NI 9216 RTD | 3 | 7 | COM | 35
Humidity Sensor | Calorimeter | NI 9205 ADC | 6 | 0 | AI0 (+) | 1 |  |  |  | Calorimeter (Sensor 1) Humidity
Humidity Sensor | Calorimeter | NI 9205 ADC | 6 | 0 | AI8 (-) | 19
Humidity Sensor | Calorimeter | NI 9205 ADC | 6 | 1 | AI1 (+) | 2 |  |  |  | Calorimeter (Sensor 2) Humidity
Humidity Sensor | Calorimeter | NI 9205 ADC | 6 | 1 | AI9 (-) | 20
Gas Flow | Calorimeter | NI 9205 ADC | 6 | 2 | AI2 (+) | 3 |  |  |  | Calorimeter Gas Flow
Gas Flow | Calorimeter | NI 9205 ADC | 6 | 2 | A10 (-) | 21
Voltage Monitor | N/A | NI 9205 ADC | 6 | 18 | AI18 (+) | 11 |  |  |  | Chassis +5V Supply Monitor
Voltage Monitor | N/A | NI 9205 ADC | 6 | 18 | A26 (-) | 29
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 0 | CH0a | 0 |  |  |  | CAEN Calorimeter HV Card 1 Enable
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 0 | CH0b | 1
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 1 | CH1a | 2 |  |  |  | CAEN Calorimeter HV Card 2 Enable
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 1 | CH1b | 3
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 2 | CH2a | 4 |  |  |  | CAEN Calorimeter HV Card 3 Enable
CAEN HV Enable | Calorimeter | NI 9485 Relay | 8 | 2 | CH2b | 5
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 3 | CH3a | 6 |  |  |  | CAEN Hodoscope HV Card 1 Enable
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 3 | CH3b | 7
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 4 | CH4a | 8 |  |  |  | CAEN Hodoscope HV Card 2 Enable
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 4 | CH4b | 9
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 5 | CH5a | 10 |  |  |  | CAEN Hodoscope HV Card 3 Enable
CAEN HV Enable | Hodoscope | NI 9485 Relay | 8 | 5 | CH5b | 11
Mpod LV Enable | Calorimeter | NI 9485 Relay | 8 | 6 | CH6a | 12 |  |  |  | Mpod Calorimeter LV Enable (+5V for enable)
Mpod LV Enable | Calorimeter | NI 9485 Relay | 8 | 6 | CH6b | 13
Mpod LV Enable | Hodoscope | NI 9485 Relay | 8 | 7 | CH7a | 14 |  |  |  | Mpod Hodoscope LV Enable (+5V for enable)
Mpod LV Enable | Hodoscope | NI 9485 Relay | 8 | 7 | CH7b | 15

## NI Components
Forward Tagger Interlock System Components (National Instruments)
Component | Part Number | Model | Details | Units
Controller | 783848-01 | cRIO-9035 | cRIO 9035 Controller and Chassis | 1
RTD Module | 783664-01 | NI 9216 with spring terminals | 8-Ch PT100 RTD 24-bit, 50S/s/ch, Analog Input Module | 1
Solid State Relay | 779600-01 | NI 9485 | 8-Ch, ±60 VDC, 750 mA (60V Ch-Ch, 250Vrms Ch-Earth Isolated) SSR C Series Module | 1
16 Ch. Analog Input | 779519-01 | NI 9205 with spring terminals | 16-Ch (Differential) ±200 mV to ±10 V, 16-Bit, 250 kS/s Analog Input Module | 1
Analog Output | 783733-01 | NI 9265 with spring terminals | 0 to 20 mA, 16-Bit, 100 kS/s, 4-Ch AO Module | 1
cRio Blanks | 196917-01 | NI 9977 | C-series Blank cRIO modules | 3
D-Sub Interface | 781922-01 | NI 9924 | Front-mount 25-pin D-SUB to screw terminals | 1
Rack Mount | 781989-01 |  | NI Rack Mount Kit for cDAQ/cRIO | 1
Rail kit | 157268-01 |  | DIN Rail Mounting Kit for 8-slot NI cRIO-9035 | 1
Power Supply | 781093-01 | NI PS-15 | Power supply, 24 VDC, 5A, 100-120/200-240 VAC Input | 1

## NI Purchase Configuration
Your Configuration ID is: CR5122167
Integrated Controller and Chassis
Part Number | Model | Description | Quantity | Price
783848-01 | NI cRIO-9035 | cRIO-9035, 1.33 GHz Dual-Core CRIO, 8-Slot, 70T FPGA, RT, Non-XT | 1 | $ 3,499
|  | Standard Repair Coverage | 1
|  |  | Subtotal: | $ 3,499
Modules
779519-01 | NI 9205 with Spring Terminals | NI 9205 32-Channel ±10 V, 250 kS/s, 16-Bit Analog Input Module | 1 | $ 881
|  | Standard Repair Coverage | 1
779567-01 | NI 9940 Extra Strain relief, operator protection (qty 1) | NI 9940 Backshell for 36-pos connector block (qty 1) | 1 | $ 31
783664-01 | NI 9216 with Spring Terminals | NI 9216 8-Ch PT100 RTD 24-Bit, 50S/S/CH, Analog Input Module | 1 | $ 950
|  | Standard Repair Coverage | 1
783733-01 | NI 9265 with Spring Terminals | NI 9265 Spring Term, 0 to 20 mA, 16-Bit, 100 kS/s, 4-Ch AO Module | 1 | $ 384
|  | Standard Repair Coverage | 1
783787-01 | NI 9981 Strain relief, operator protection (qty 1) | NI 9981, Strain Relief and Operator Protection (qty 1) | 1 | $ 30
779351-01 | NI 9401 with DSub | NI 9401 8-Channel, 100 ns, TTL Digital Input/Output Module | 1 | $ 296
|  | Standard Repair Coverage | 1
781922-01 | NI 9924, Front-mount 25-pin D-SUB to screw terminals | NI 9924 Front-mount terminal block for 25-pin D-Sub Modules | 1 | $ 103
779600-01 | NI 9485 | NI 9485 8-Ch, ±60 VDC, 750 mA SSR C Series Module | 1 | $ 351
|  | Standard Repair Coverage | 1
192692-01 | NI 9939 Strain relief, operator protection (qty 1) | NI 9939 Backshell for 16-pos connector block (qty 1) | 1 | $ 31
|  |  | Subtotal: | $ 3,057
System Accessories
781989-01 | Rack Mount Kit | NI Rack Mount Kit for cDAQ/cRIO | 1 | $ 453
157268-01 | DIN Rail Mounting Kit for cRIO-903X (8 slots) | DIN Rail Mounting Kit for 8-Slot NI cRIO-903x and NI cDAQ-9133/35 | 1 | $ 31
781093-01 | PS-15, 5Amp, 24VDC | NI PS-15 Power Supply, 24 VDC, 5 A, 100-120/200-240 VAC Input | 1 | $ 221
|  | Standard Repair Coverage | 1
196917-01 | NI 9977 C Series Filler Module for Empty Slot | NI 9977 C Series Filler Module for Empty Slot | 3 | $ 31
|  |  | Subtotal: | $ 798
Services
SRV-CR5122167 | Standard Services | Standard Service Program for CompactRIO Systems | 1 | $ 531.50
|  |  | Subtotal: | $ 531.50
|  |  | Total: | $ 7,885.50
|  |  | Discounted Total: | $ 7,885.50
|  |  | You Save: | $ 93.79 (1%)
National Instruments Corporation
11500 N Mopac Expwy
Austin, TX 78759-3504
Phone: (800) 531-5066
Fax: 512-683-8411