## Sheet1
Parameters of ESR and Halls A, B, and C to help operators to understand the complete system, its status and effect of your changes on others
Revision | 1_5
Date | 2017-11-01
Last updated by | David Kashy | [5 empty] | Averages
Sub System |  | New name | Original name | Normal Min | Normal Max | Current Value | last 2 hrs | last 8 hrs | yesterday | last week | Comments
Hall Warm Gas and Recovery Compressors/Purifiers
CPI0840 | atm | Recovery Suction Pressure | Recovery compressor suction pressure | 1.03 | 1.08 | [5 empty] | If rising the Purifier could be overloaded from too much Hall warm return flow
CFI082 | g/s | Purifier Flow Rate | Purifier Flow Rate | 5 | 20
CPV084BY | % | Recovery Bypass Valve | Recovery compressor bypass valve position | -3 | 50?
CPV10DR | % | Storage Tank Cleanup Valve
CFI60DLP | g/s | Dirty Flow from 3 Halls | Dirty return flow rate from Halls A, B, C | 0 | 20
CPI6010 | atm | 4atm warm He sup press | 4 atm Helium warm gas supply pressure | 3.9 | 4.8
CFI6010 | g/s | 4atm warm He sup flow | 4 atm Helium warm gas supply flow rate | 0 | 15
CFI75DB15R | g/s | 4atm warm He to Hall A | 4 atm Helium warm gas to Hall A DBX | 1 | 10
B_TORUS:LHe:FI8561_Flow | g/s | 4atm warm He to Hall B | 4 atm Helium warm gas to Hall B DBX | 0 | 10
MV6010A | Open/Closed | 4atm to Hall A | 4 atm Helium manual valve to Hall A | N/A | N/A | [5 empty] | User input or need to add readback
MV6010B | Open/Closed | 4atm to Hall B | 4 atm Helium manual valve to Hall B | N/A | N/A | [5 empty] | User input or need to add readback
MV6010C | Open/Closed | 4atm to Hall C | 4 atm Helium manual valve to Hall C | N/A | N/A | [5 empty] | User input or need to add readback
MV6030A | Open/Closed | A Warm Return to ESR | Lead and quench return to ESR from Hall A | N/A | N/A | [5 empty] | User input or need to add readback
MV6031A | Open/Closed | A Warm Return to Recovery | Lead and quench return to Purifier from Hall A | N/A | N/A | [5 empty] | User input or need to add readback
MV6030B | Open/Closed | B Warm Return to ESR | Lead and quench return to ESR from Hall B | N/A | N/A | [5 empty] | User input or need to add readback
MV6031B | Open/Closed | B Warm Return to Recovery | Lead and quench return to Purifier from Hall B | N/A | N/A | [5 empty] | User input or need to add readback
MV6030C | Open/Closed | C Warm Return to ESR | Lead and quench return to ESR from Hall C | N/A | N/A | [5 empty] | User input or need to add readback
MV6031C | Open/Closed | C Warm Return to Recovery | Lead and quench return to Purifier from Hall C | N/A | N/A | [5 empty] | User input or need to add readback
CFI6030 | g/s | Clean return flow from 3 Halls | Clean return flow from Halls A, B, C | 0 | 20
ESR Coldbox, Dewar and Valve Box
CPI60HP | atm |  | High Pressure Helium into cold box | 15 | 18 | [5 empty] | ESR Cold Box fully loaded at 18g/s
CPI60LP | atm |  | Low Pressure Helium from cold box | 1.03 | 1.08
CPI671 | atm | ESR VB 4K supply pressure to Halls | ESR Valve Box 4K supply pressure to Halls | 2.8 | 3.2 | [5 empty] | Normal is 3.1 if below 3.0 then ESR at 100% capatity
CPI672 | atm | ESR VB 4K return pressure from Halls | ESR Valve Box 4K return pressure from Halls | 1.05 | 1.15
CPI673 | atm | ESR VB 15K supply pressure to Halls | ESR Valve Box 15K supply pressure to Halls
CPI674 | atm | ESR VB 20K supply pressure from Halls | ESR Valve Box 20K supply pressure to Halls
CPI6751 | atm | ESR VB 80K supply pressure to Halls | ESR Valve Box 80K supply pressure to Halls | 3.5 | 4
CLL6763A | % | 10K liter Helium Dewar at ESR | 10K liter Helium Dewar at ESR | 30 | 80
CLL6763A_DL_Dt30 | %/hr | 10K Dewar level change rate 0.5hr | 10K liter Helium Dewar level change rate over last 1/2hr | [7 empty] | Calculated value
CLL6763A_DL_Dt120 | %/hr | 10K Dewar level change rate 2hr | 10K liter Helium Dewar level change rate over last 2 hrs | [7 empty] | Calculated value
CLL6763A_DL_Dt600 | %/hr | 10K Dewar level change rate 10hr | 10K liter Helium Dewar level change rate over last 10 hrs | [7 empty] | Calculated value
CEV6761.ORBV | % | 10K Dewar fill valve | 10,000 liter helium dewar at ESR supply valve | 0 | 100 | [5 empty] | IF closed then ESR at 100% capacity
CFI6711A | g/s | 4K supply flow to Hall A | 4K supply flow to Hall A
CFI6711B | g/s | 4K supply flow to Hall B | 4K supply flow to Hall B | 5 | 15 | [5 empty] | Is bi-stable and jumps ~factor of 2 w/o valve changes
CFI6711C | g/s | 4K supply flow to Hall C | 4K supply flow to Hall C
CFI6712 | g/s | 4K flow via ESTL to ESR | 4K supply flow from CHL to ESR via ESTL | 0 | 20 | [5 empty] | Used to boost ESR capacity (cool magnets or fill Dewar
Hall A Magnets and Target
CLL71Q205R | % |  | Helium level Left Arm Magnet Q2 | 0 | 100 | 90 |  |  |  |  | Trip point 60%
CLL71Q305R | % |  | Helium level Left Arm Magnet Q3 | 0 | 100 | 90 |  |  |  |  | Trip point 60%
CLL71D106R | % |  | Helium level Left Arm Magnet D1 | 0 | 100 | 85 |  |  |  |  | Trip point 40%
CLL72Q205R | % |  | Helium level Right Arm Magnet Q2 | 0 | 100 | 90 |  |  |  |  | Trip point 60%
CLL72Q305R | % |  | Helium level Right Arm Magnet Q3 | 0 | 100 | 90 |  |  |  |  | Trip point 60%
CLL72D106R | % |  | Helium level Right Arm Magnet D1 | 0 | 100 | 85 |  |  |  |  | Trip point 40%
HacL_Q2_HP3458A:IOUT | I |  | Left Q2 I OUT | 0 | 1722.3995
HacL_HPE1313A:0_Ch21 | SLM |  | Left Q2 Lead A | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
HacL_HPE1313A:0_Ch22 | SLM |  | Left Q2 Lead B | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
HacL_D1_HP3458A:IOUT | I |  | Left Dipole I OUT | 0 | 1495.1533
HacL_HPE1313A:0_Ch0 | SLM |  | Left Dipole Lead A | 0 | 100 | [5 empty] | Trip point 40 slm, normal operation 80 slm
HacL_HPE1313A:0_Ch1 | SLM |  | Left Dipole Lead B | 0 | 100 | [5 empty] | Trip point 40 slm, normal operation 80 slm
HacL_Q3_HP3458A:IOUT | I |  | LEFT Q3 I OUT | 0 | 1592.4747
HacL_HPE1313A:0_Ch32 | SLM |  | Left Q3 Lead A | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 100 slm
HacL_HPE1313A:0_Ch33 | SLM |  | Left Q3 Lead B | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 100 slm
HacR_Q2_HP3458A:IOUT | I |  | Right Q2 I OUT | 0 | 1359.9608
HacR_HPE1313A:0_Ch21 | SLM |  | Right Q2 Lead A | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
HacR_HPE1313A:0_Ch22 | SLM |  | Right Q2 Lead B | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
HacR_D1_HP3458A:IOUT | I |  | Right Dipole I OUT | 0 | 1140
HacR_HPE1313A:0_Ch0 | SLM |  | Right Dipole Lead A | 0 | 100 | [5 empty] | Trip point 40 slm, normal operation 80 slm
HacR_HPE1313A:0_Ch1 | SLM |  | Right Dipole Lead B | 0 | 100 | [5 empty] | Trip point 40 slm, normal operation 80 slm
HacR_Q3_HP3458A:IOUT | I |  | Right Q3 I OUT | 0 | 1257.3917
HacR_HPE1313A:0_Ch32 | SLM |  | Right Q3 Lead A | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
HacR_HPE1313A:0_Ch33 | SLM |  | Right Q3 Lead B | 0 | 100 | [5 empty] | Trip point 50 slm, normal operation 80 slm
CFI75DB15O | g/s |  | 4 Atom flow (needs calibration) | 0 |  | 0
CPI75DB05RA | Atm | 4K supply Hall A DC | 4K He supply pressure (distribution can) | 0 | 100 | 3.1
CPI75DB08RA | Atm | 4K return Hall A DC | 4K He Return pressure (distribution can) (needs calibration) | 0 | 100 | 1.8
CEV71D104R.ORBV | % |  | Top fill Left Dipole | 0 | 100
CEV71D116R.ORBV | % |  | Bottom Fill Left Dipole | 0 | 100
CEV71D105R.ORBV | % |  | Cold Return Left Dipole | 0 | 100
CEV71D106R.ORBV | % |  | Warm Return Left Dipole | 0 | 100
CEV72D104R.ORBV | % |  | Top fill Right Dipole | 0 | 100
CEV72D116R.ORBV | % |  | Bottom Fill Right Dipole | 0 | 100
CEV72D105R.ORBV | % |  | Cold Return Right Dipole | 0 | 100
CEV72D106R.ORBV | % |  | Warm Return Right Dipole | 0 | 100 | [5 empty] | Read back scaling needs work
CEV71Q204R.ORBV | % |  | Top fill Left Q2 | 0 | 100
CEV71Q216R.ORBV | % |  | Bottom Fill Left Q2 | 0 | 100
CEV71Q206R.ORBV | % |  | Warm Return Left Q2 | 0 | 100
CEV72Q204R.ORBV | % |  | Top fill Right Q2 | 0 | 100
CEV72Q216R.ORBV | % |  | Bottom Fill Right Q2 | 0 | 100
CEV72Q206R.ORBV | % |  | Warm Return Right Q2 | 0 | 100 | [5 empty] | Read back scaling needs work
CEV71Q304R.ORBV | % |  | Top fill Left Q3 | 0 | 100
CEV71Q316R.ORBV | % |  | Bottom Fill Left Q3 | 0 | 100
CEV71Q306R.ORBV | % |  | Warm Return Left Q3 | 0 | 100
CEV72Q304R.ORBV | % |  | Top fill Right Q3 | 0 | 100
CEV72Q316R.ORBV | % |  | Bottom Fill Right Q3 | 0 | 100
CEV72Q306R.ORBV | % |  | Warm Return Right Q3 | 0 | 100 | [5 empty] | Read back scaling needs work
Hall B Magnets, Buffer Dewar and Target
B_SOL:LHe:EV8611JT | % | Sol 4K Supply Valve | 4K supply Valve position
B_SOL:LHe:EV8611CD | % | Sol CD Supply Valve | Cooldown Supply Valve position
B_SOL:LHe:LL8620DP | % | Sol Lead Reservoir LL DP probe | Helium level in Solenoid Lead reservoir (Differential Pressure sensor) | 90 | 100
B_SOL:LHe:LL8620SC | % | Sol Lead Reservoir LL SC probe | Helium level in Solenoid Lead reservoir (Superconducting sensor) | 90 | 100 | [5 empty] | Not used in control (always 100%)
B_SOL:LHe:LL8670DP | % | Sol Mag Reservoir LL DP probe | Helium level in Solenoid Magnet reservoir (DP sensor) | 70 | 90
B_SOL:LHe:LL8670SC | % | Sol Mag Reservoir LL SC probe | Helium level in Solenoid Magnet reservoir (SC sensor) | 70 | 90 | [5 empty] | Used in control
B_SOL:MPS:I_ZFCT | Amps | Solenoid Current | Solenoid Current | -2416 | 2416
B_SOL:LHe:FI8621A_IN | SLM | Solenoid VCL flow A | Solenoid VCL flow A | 60 | 70
B_SOL:LHe:FI8621B_IN | SLM | Solenoid VCL flow B | Solenoid VCL flow B | 60 | 70
B_TORUS:LHe:PV8522SR | % | Solenoid cold return valve | Solenoid cold return valve | 4 | 58
B_TORUS:LHe:PV8522SCD | % | Solenoid warm return valve | Solenoid cooldown (warm return) valve | 0 | 0
B_TORUS:LHe:EV8115JT | % | Torus 4K Supply Valve | 4K Supply Valve position
B_TORUS:LHe:EV8111CD | % | Torus 4K Supply bottom fill | Cooldown Supply valve (bottom fill)
B_TORUS:LHe:EV8111BY | % | Torus 4K Bypass valve | 4K Bypass valve | 0 | 0
B_TORUS:LHe:LL8120DP | % | Torus LL DP probe | Helium level in Torus (Differential Pressure sensor) | 60 | 80
B_TORUS:LHe:LL8120SC | % | Torus LL SC probe | Helium level in Torus (Superconducting sensor) | 100 | 100 | [5 empty] | Not used in control (always 100%)
B_TORUS:MPS:I_ZFCT | Amps | Torus Current | Torus Current | -3770 | 3770
B_TORUS:LHe:FV8121A_IN | SLM | Torus VCL flow A | Torus VCL flow A | 88 | 111
B_TORUS:LHe:FV8121B_IN | SLM | Torus VCL flow B | Torus VCL flow B | 88 | 111
B_TORUS:LHe:PV8522TR | % | Torus cold return valve | Torus cold return valve | 45 | 65
B_TORUS:LHe:PV8522TCD | % | Torus warm return valve | Torus cooldown (warm return) valve | 0 | 0
LL8210.VAL | % | Buffer Dewar LL SC probe | Helium level in Buffer Dewar | 55 | 65
EV8210BP.ORBV |  | Buffer Dewar cold return valve | Buffer Dewar cold return valv | 20 | 50
EV8210CD_readback |  | Buffer Dewar warm return valve | Buffer Dewar warm return valve (manual ball valve) | 0 | 2
B_SACLAYTGT:LT_CR | % | Saclay Target LHe LL | Helium Level in Saclay Target | 0 | 100 | [5 empty] | Sometimes runs in batch fill mode
B_SACLAYTGT:PT_2KH | mbar | Target coolant (LHe) pressure | Helium pressure in Target gas condensor | 50 | 1300 | [5 empty] | When subatmospheric running He4 or He3 target
B_SACLAYTGT:TT_ET | K | Target Temperature | Target Temperature | 3 | 300
Hall C Magnets and Target
ecQ1_h_LHe | % |  | Helium level HMS Q1 | 60 | 80
ecQ2_h_LHe | % |  | Helium level HMS Q2 | 60 | 80
ecQ3_h_LHe | % |  | Helium level HMS Q3 | 60 | 80
ecDI_h_LHe | % |  | Helium level HMS Dipole | 60 | 80
ecSHB_h_LHe | % |  | Helium level SHMS HB | 60 | 80
ecSQ1_h_LHe | % |  | Helium level SHMS Q1 | 60 | 80
ecSQ2_h_LHe | % |  | Helium level SHMS Q2 | 60 | 80
ecSQ3_h_LHe | % |  | Helium level SHMS Q3 | 60 | 80
ecSDI_h_LHe | % |  | Helium level SHMS Dipole | 60 | 80
ecQ1_I_True | Amps |  | Current HMS Q1 | 0 | 1100
ecQ2_I_True | Amps |  | Current HMS Q2 | 0 | 1100
ecQ3_I_True | Amps |  | Current HMS Q3 | 0 | 1100
ecDI_I_True | Amps |  | Current HMS Dipole | 0 | 3000
ecSHB_I_True | Amps |  | Current SHMS HB | 0 | 3950
ecSQ1_I_True | Amps |  | Current SHMS Q1 | 0 | 3500
ecSQ2_I_True | Amps |  | Current SHMS Q2 | 0 | 3660
ecSQ3_I_True | Amps |  | Current SHMS Q3 | 0 | 2500
ecSDI_I_True | Amps |  | Current SHMS Dipole | 0 | 3450
ecQ1_m_flow_CL_P | l/min |  | HMS Q1 VCL + Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecQ1_m_flow_CL_N | l/min |  | HMS Q1 VCL - Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecQ2_m_flow_CL_P | l/min |  | HMS Q2 VCL + Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecQ2_m_flow_CL_N | l/min |  | HMS Q2 VCL - Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecQ3_m_flow_CL_P | l/min |  | HMS Q3 VCL + Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecQ3_m_flow_CL_N | l/min |  | HMS Q3 VCL - Flow | 9 | 25 | [5 empty] | adjusted according to PSU output current
ecDI_M_flow_Rx | l/hr |  | HMS Dipole VCL + Flow | 3300 | 7500 | [5 empty] | adjusted according to PSU output current
ecDI_M_flow_Lx | l/hr |  | HMS Dipole VCL - Flow | 3300 | 7500 | [5 empty] | adjusted according to PSU output current
ecSHB_m_flow_CL_R | l/min |  | SHMS HB VCL + Flow | 50 | 110 | [5 empty] | adjusted according to PSU output current
ecSHB_m_flow_CL_L | l/min |  | SHMS HB VCL - Flow | 50 | 110 | [5 empty] | adjusted according to PSU output current
ecSQ1_m_flow_CL_R | l/min |  | SHMS Q1 VCL + Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecSQ1_m_flow_CL_L | l/min |  | SHMS Q1 VCL - Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecSQ2_m_flow_CL_R | l/min |  | SHMS Q2 VCL + Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecSQ2_m_flow_CL_L | l/min |  | SHMS Q2 VCL - Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecSQ3_m_flow_CL_R | l/min |  | SHMS Q3 VCL + Flow | 50 | 90 | [5 empty] | adjusted according to PSU output current
ecSQ3_m_flow_CL_L | l/min |  | SHMS Q3 VCL - Flow | 50 | 90 | [5 empty] | adjusted according to PSU output current
ecSDI_m_flow_CL_R | l/min |  | SHMS Dipole VCL + Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecSDI_m_flow_CL_L | l/min |  | SHMS Dipole VCL - Flow | 50 | 100 | [5 empty] | adjusted according to PSU output current
ecDI_S5_LVDT_true |  |  | HMS DI 4K Supply Valve
ecQ3_V8_LVDT_true |  |  | HMS Q3 4K Supply Valve
ecQ2_V8_LVDT_true |  |  | HMS Q2 4K Supply Valve
ecQ1_V8_LVDT_true |  |  | HMS Q1 4K Supply Valve
ecDI_S6_LVDT_true |  |  | HMS DI 4K Return Valve
ecQ3_V13_LVDT_true |  |  | HMS Q3 4K Return Valve
ecQ2_V13_LVDT_true |  |  | HMS Q2 4K Return Valve
ecQ1_V13_LVDT_true |  |  | HMS Q1 4K Return Valve
ecQ1_vWR_LVDT_true |  |  | HMS DI Warm Return Valve
ecQ2_vWR_LVDT_true |  |  | HMS Q3 Warm Return Valve
ecQ3_vWR_LVDT_true |  |  | HMS Q2 Warm Return Valve
ecDI_s11_LVDT_true |  |  | HMS Q1 Warm Return Valve
ecSDI_V5_LVDT_true |  |  | SHMS DI 4K Supply Valve
ecSQ3_V5_LVDT_true |  |  | SHMS Q3 4K Supply Valve
ecSQ2_V5_LVDT_true |  |  | SHMS Q2 4K Supply Valve
ecSQ1_V5_LVDT_true |  |  | SHMS Q1 4K Supply Valve
ecSHB_V5_LVDT_true |  |  | SHMS HB 4K Supply Valve
ecSDI_V6_LVDT_true |  |  | SHMS DI 4K Return Valve
ecSQ3_V6_LVDT_true |  |  | SHMS Q3 4K Return Valve
ecSQ2_V6_LVDT_true |  |  | SHMS Q2 4K Return Valve
ecSQ1_V6_LVDT_true |  |  | SHMS Q1 4K Return Valve
ecSHB_V6_LVDT_true |  |  | SHMS HB 4K Return Valve
ecSDI_vWR_LVDT_true |  |  | SHMS DI Warm Return Valve
ecSHB_vWR_LVDT_true |  |  | SHMS Q3 Warm Return Valve
ecSQ1_vWR_LVDT_true |  |  | SHMS Q2 Warm Return Valve
ecSQ2_vWR_LVDT_true |  |  | SHMS Q1 Warm Return Valve
ecSQ3_vWR_LVDT_true |  |  | SHMS HB Warm Return Valve
CEV6711C.ORBV | % |  | Cryo's 4K Supply Valve to Hall C | 100 | 100
CEV6721C.ORBV | % |  | Cryos's 4K Return Valve from Hall C | 100 | 100
CEV6711C | g/s |  | Cryo's 4K Flow Limit | [7 empty] | Input from Cryo
CFI6711C | g/s |  | 4K Supply Flow to Hall C | 20 | 25
echmst1 | K |  | HMS Transfer Line He Supply Temp | 5.1 | 5.3
echmst2 | K |  | HMS Transfer Line He Return Temp | 5.2 | 5.4
ecSTL_T_He_Supply_TL | K |  | SHMS Transfer Line He Supply Temp | 5.5 | 6.5
ecSTL_T_He_Return_TL | K |  | SHMS Transfer Line He Return Temp | 5.1 | 5.3
Moller Magnet Hall C
EV91017_readback | % |  | 4K He Supply Valve
EV91019_readback | % |  | 4K He Return Valve
LL91020 | % |  | He Liquid Level
EV91001_pos | % |  | 300K warm He gas return valve
OXSS_RDF | T |  | B-Field Leads (no current readback)
OXSS_MGFD | T |  | B_Field presistent
Atarg: Hall A Cryotarget
Sub System |  |  |  | Normal Min | Normal Max | Current Value | last 2 hrs | last 8 hrs | yesterday | last week | Comments
haL1_JTV_Rca | % open |  | Loop 1 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in use
haL1_Temperature | K |  | Loop 1control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
haL1_hp_power_R | Watts |  | Loop 1 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
haL1_TI_Cryo_In_R | K |  | Loop 1 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
haL1_TI_Cryo_Out_R | K |  | Loop 1 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
haL2_JTV_Rca | % open |  | Loop 2 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in operation
haL2_Temperature | K |  | Loop 2 control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
haL2_hp_power_R | Watts |  | Loop 2 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
haL2_TI_Cryo_In_R | K |  | Loop 2 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
haL2_TI_Cryo_Out_R | K |  | Loop 2 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
haL3_JTV_Rca | % open |  | Loop 3 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in operation
haL3_Temperature | K |  | Loop 3 control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
haL3_hp_power_R | Watts |  | Loop 3 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
haL3_TI_Cryo_In_R | K |  | Loop 3 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
haL3_TI_Cryo_Out_R | K |  | Loop 3 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
haLS218_4_T4 | K |  | Warm return temperature | 280 | 300 | [5 empty] | May be colder during initial cooling of target
haWR_EV_R | % open |  | Warm return valve | 0 | 0 | [5 empty] | May be open during initial cooling of target
haCryo_Supply_T | K |  | ESR 15K supply temperature to Hall A | 13 | 16 | [5 empty] | ESR signal, with Target Group name
haCryo_Return_T | K |  | ESR 15K return temperature from Hall A | 18 | 25 | [5 empty] | ESR signal, with Target Group name
haCryo_Supply_P | atm |  | ESR 15K supply pressure to Hall A | [7 empty] | ESR signal, with Target Group name
haCryo_Return_P | atm |  | ESR 15K return pressure from Hall A | [7 empty] | ESR signal, with Target Group name
haHallA_beam_current | microAmps |  | beam current on Hall A cryotarget
Ctarg: Hall C Cryotarget
Sub System |  |  |  | Normal Min | Normal Max | Current Value | last 2 hrs | last 8 hrs | yesterday | last week | Comments
hcL1_JTV_Rca | % open |  | Loop 1 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in use
hcL1_Temperature | K |  | Loop 1control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
hcL1_hp_power_R | Watts |  | Loop 1 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
hcL1_TI_Cryo_In_R | K |  | Loop 1 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
hcL1_TI_Cryo_Out_R | K |  | Loop 1 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
hcL2_JTV_Rca | % open |  | Loop 2 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in operation
hcL2_Temperature | K |  | Loop 2 control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
hcL2_hp_power_R | Watts |  | Loop 2 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
hcL2_TI_Cryo_In_R | K |  | Loop 2 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
hcL2_TI_Cryo_Out_R | K |  | Loop 2 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
hcL3_JTV_Rca | % open |  | Loop 3 coolant valve | 15 | 50 | [5 empty] | may be zero if Loop not in operation
hcL3_Temperature | K |  | Loop 3 control temperature, readback | 18 | 24 | [5 empty] | value depends on loop fluid (LH2 or LD2)
hcL3_hp_power_R | Watts |  | Loop 3 control heater | 0 | 500 | [5 empty] | may be zero if Loop not in use
hcL3_TI_Cryo_In_R | K |  | Loop 3 coolant-in temperature | 13 | 16 | [5 empty] | may be higher if Loop not in use
hcL3_TI_Cryo_Out_R | K |  | Loop 3 coolant-out temperature | 18 | 25 | [5 empty] | may be higher in Loop not in use
hcLS218_4_T4 | K |  | Warm return temperature | 280 | 300 | [5 empty] | May be colder during initial cooling of target
hcWR_EV_R | % open |  | Warm return valve | 0 | 0 | [5 empty] | May be open during initial cooling of target
hcCryo_Supply_T | K |  | ESR 15K supply temperature to Hall C | 13 | 16 | [5 empty] | ESR signal, with Target Group name
hcCryo_Return_T | K |  | ESR 15K return temperature from Hall C | 18 | 25 | [5 empty] | ESR signal, with Target Group name
hcCryo_Supply_P | atm |  | ESR 15K supply pressure to Hall C | [7 empty] | ESR signal, with Target Group name
hcCryo_Return_P | atm |  | ESR 15K return pressure from Hall C | [7 empty] | ESR signal, with Target Group name
hcHallC_beam_current | microAmps |  | beam current on Hall C cryotarget
UPDATED 10_30_17
Seem to be correct already 10_30_17