## Sheet1
PV | Type | Deadband | Notes
B_BONUS_GAS_Error | bool |  | True = Fault
B_BONUS_GAS_FGD | bool |  | True = Flammable Gas Detected
B_BONUS_GAS_MFC104_Flow | single | 0.1 | flow readback in sccm
B_BONUS_GAS_MFC104_Flow_Set | single | 0 | flow setpoint, no dead-band
B_BONUS_GAS_MFC104_Temp | single | 1 | MFC temp degC
B_BONUS_GAS_MFC104_Valve | single | 1 | Valve Position in %
B_BONUS_GAS_MFC104_Gas | enum |  | 0 = H2, 1 = D2, 2 = He4, 3 = N2
B_BONUS_GAS_Mode | enum |  | 0 = Failure, 1 = Auto, 2 = Manual, 3 = Purge - Empty, 4 = Purge - Fill
B_BONUS_GAS_PT104 | double | 1 | Gas Pad Pressure, psig
B_BONUS_GAS_PT110 | double | 1 | Gas Panel Pressure, psig
B_BONUS_GAS_PT406 | double | 1 | N2 Purge Pressure, psig
B_BONUS_GAS_SVBT100 | bool |  | True = Open, flammable gas supply
B_BONUS_GAS_SVBT102 | bool |  | True = Open, non-flammable gas supply
B_BONUS_GAS_SVBT108 | bool |  | True = Open, target straw supply
B_BONUS_GAS_SVBT112 | bool |  | True = Open, target straw exhaust
B_BONUS_GAS_SVBD206 | bool |  | True = Open, He Buffer supply