## NI Signals from Patch Panel
SVT Hardware Interlock Connections / Signals from Patch Panel Blocks
2015-08-13
Category | # | SVT Region | SVT Sector / Module | NI cRio Module Type | cRio Slot # | cRio Channel + | cRio Connector Pin | Hardware Interlock Cable ID | Patch Panel Block Number | Block Pin # | EPICS SC Cable ID | VME Slot # | VME Board Type | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Main Control System Signal Name | Comments
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0+ | HFCB_R1_M1 | 1 | 1 | HFCB_R1_M1 | 2 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0- |  | 1 | 14 | HFCB_R1_M1 | 2 | V450 | J1 | 14 | CH 0-
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1+ | HFCB_R2_M1 | 3 | 5 | HFCB_R2_M1 | 3 | V450 | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1- |  | 3 | 18 | HFCB_R2_M1 | 3 | V450 | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2+ | HFCB_R3_M1 | 7 | 1 | HFCB_R3_M1 | 5 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2- |  | 7 | 14 | HFCB_R3_M1 | 5 | V450 | J1 | 14 | CH 0-
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3+ | HFCB_R4_M1 | 13 | 1 | HFCB_R4_M1 | 8 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3- |  | 13 | 14 | HFCB_R4_M1 | 8 | V450 | J1 | 14 | CH 0-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | EX0 | DET_INT_TEMP_SB3 | 3 | 11 | RTD_B3_T2 | 3 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0+ |  | 3 | 24 | RTD_B3_T2 | 3 | V450 | J1 | 24 | RtdB E-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0- |  | 3 | 12 | RTD_B3_T2 | 3 | V450 | J1 | 12 | RtdB S+
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | COM |  | 3 | 25 | RTD_B3_T2 | 3 | V450 | J1 | 25 | RtdB S-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | EX1 | DET_INT_TEMP_SB6 | 6 | 11 | RTD_B6_T2 | 4 | V450 | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1+ |  | 6 | 24 | RTD_B6_T2 | 4 | V450 | J2 | 24 | RtdD E-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1- |  | 6 | 12 | RTD_B6_T2 | 4 | V450 | J2 | 12 | RtdD S+
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | COM |  | 6 | 25 | RTD_B6_T2 | 4 | V450 | J2 | 25 | RtdD S-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | EX2 | DET_INT_TEMP_SB9 | 9 | 11 | RTD_B9_T2 | 6 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2+ |  | 9 | 24 | RTD_B9_T2 | 6 | V450 | J1 | 24 | RtdB E-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2- |  | 9 | 12 | RTD_B9_T2 | 6 | V450 | J1 | 12 | RtdB S+
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | COM |  | 9 | 25 | RTD_B9_T2 | 6 | V450 | J1 | 25 | RtdB S-
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI0 (+) | DET_INT_HUM_SB3 | 19 | 6 |  | 11 | V450 | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI8 (-) |  | 19 | 19 |  | 11 | V450 | J1 | 19 | CH 5-
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI1 (+) | DET_INT_HUM_SB6 | 20 | 4 |  | 11 | V450 | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI9 (-) |  | 20 | 17 |  | 11 | V450 | J2 | 17 | CH 11-
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI2 (+) | DET_INT_HUM_SB9 | 22 | 6 |  | 12 | V450 | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI10 (-) |  | 22 | 19 |  | 12 | V450 | J2 | 19 | CH 13-
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0+ | COOL_FLOW_R1_R3 | 21 | 4 |  | 12 | V450 | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R1-R3)
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0- |  | 21 | 17 |  | 12 | V450 | J1 | 17 | CH 3-
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1+ | COOL_FLOW_R1_R4 | 21 | 5 |  | 12 | V450 | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R4)
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1- |  | 21 | 18 |  | 12 | V450 | J1 | 18 | CH 4-
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2+ | COOL_TEMP | 21 | 2 |  | 12 | V450 | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2- |  | 21 | 15 |  | 12 | V450 | J1 | 15 | CH 1-

## NI Signals
SVT Hardware Interlock Signals by cRio Channels
2015-08-13
Category | # | SVT Region | SVT Sector / Module | NI cRio Module Type | cRio Slot # | cRio Channel + | cRio Connector Pin | Hardware Interlock Cable ID | Interlock System Cable Asssembly Type | Patch Panel Block Number | Block Pin # | EPICS SC Cable ID | VME Slot # | VME Board Type | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Main Control System Signal Name | Comments
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0+ | HFCB_R1_M1 | HFCB Temperature Cable Assemblies | 1 | 1 | HFCB_R1_M1 | 2 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | 1 | NI 9239 ADC | 1 | 0 | AI0- |  |  | 1 | 14 | HFCB_R1_M1 | 2 | V450 | J1 | 14 | CH 0-
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1+ | HFCB_R2_M1 | HFCB Temperature Cable Assemblies | 3 | 5 | HFCB_R2_M1 | 3 | V450 | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 2 | 1 | NI 9239 ADC | 1 | 1 | AI1- |  |  | 3 | 18 | HFCB_R2_M1 | 3 | V450 | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2+ | HFCB_R3_M1 | HFCB Temperature Cable Assemblies | 7 | 1 | HFCB_R3_M1 | 5 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 3 | 1 | NI 9239 ADC | 1 | 2 | AI2- |  |  | 7 | 14 | HFCB_R3_M1 | 5 | V450 | J1 | 14 | CH 0-
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3+ | HFCB_R4_M1 | HFCB Temperature Cable Assemblies | 13 | 1 | HFCB_R4_M1 | 8 | V450 | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 4 | 1 | NI 9239 ADC | 1 | 3 | AI3- |  |  | 13 | 14 | HFCB_R4_M1 | 8 | V450 | J1 | 14 | CH 0-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | EX0 | DET_INT_TEMP_SB3 | Detector Temperature Cable Extension Assemblies | 3 | 11 | RTD_B3_T2 | 3 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0+ |  |  | 3 | 24 | RTD_B3_T2 | 3 | V450 | J1 | 24 | RtdB E-
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | RTD0- |  |  | 3 | 12 | RTD_B3_T2 | 3 | V450 | J1 | 12 | RtdB S+
RTD Temp | 5 | 2 | N/A | NI 9217 RTD | 3 | 0 | COM |  |  | 3 | 25 | RTD_B3_T2 | 3 | V450 | J1 | 25 | RtdB S-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | EX1 | DET_INT_TEMP_SB6 | Detector Temperature Cable Extension Assemblies | 6 | 11 | RTD_B6_T2 | 4 | V450 | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1+ |  |  | 6 | 24 | RTD_B6_T2 | 4 | V450 | J2 | 24 | RtdD E-
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | RTD1- |  |  | 6 | 12 | RTD_B6_T2 | 4 | V450 | J2 | 12 | RtdD S+
RTD Temp | 6 | 3 | N/A | NI 9217 RTD | 3 | 1 | COM |  |  | 6 | 25 | RTD_B6_T2 | 4 | V450 | J2 | 25 | RtdD S-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | EX2 | DET_INT_TEMP_SB9 | Detector Temperature Cable Extension Assemblies | 9 | 11 | RTD_B9_T2 | 6 | V450 | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2+ |  |  | 9 | 24 | RTD_B9_T2 | 6 | V450 | J1 | 24 | RtdB E-
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | RTD2- |  |  | 9 | 12 | RTD_B9_T2 | 6 | V450 | J1 | 12 | RtdB S+
RTD Temp | 7 | 4 | 19 | NI 9217 RTD | 3 | 2 | COM |  |  | 9 | 25 | RTD_B9_T2 | 6 | V450 | J1 | 25 | RtdB S-
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | EX0 | DET_AMB_TEMP_T1 | Ambient Temperature Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Environmental Temperature Sensor - T1
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | RTD0+ |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | RTD0- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 14 | N/A | N/A | NI 9217 RTD | 4 | 0 | COM |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | EX1 | DET_AMB_TEMP_T2 | Ambient Temperature Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Environmental Temperature Sensor - T2
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | RTD1+ |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | RTD1- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RTD Temp | 15 | N/A | N/A | NI 9217 RTD | 4 | 1 | COM |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI0 (+) | DET_INT_HUM_SB3 | Detector Humidity Cable Extension Assemblies | 19 | 6 |  | 11 | V450 | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor | 8 | 2 | N/A | NI 9205 ADC | 6 | 0 | AI8 (-) |  |  | 19 | 19 |  | 11 | V450 | J1 | 19 | CH 5-
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI1 (+) | DET_INT_HUM_SB6 | Detector Humidity Cable Extension Assemblies | 20 | 4 |  | 11 | V450 | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor | 9 | 3 | N/A | NI 9205 ADC | 6 | 1 | AI9 (-) |  |  | 20 | 17 |  | 11 | V450 | J2 | 17 | CH 11-
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI2 (+) | DET_INT_HUM_SB9 | Detector Humidity Cable Extension Assemblies | 22 | 6 |  | 12 | V450 | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 10 | 4 | 19 | NI 9205 ADC | 6 | 2 | AI10 (-) |  |  | 22 | 19 |  | 12 | V450 | J2 | 19 | CH 13-
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 3 | AI3 (+) | DET_AMB_HUM_H1 | Ambient Humidity Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Humidity Sensor - Humidity Sensor 1
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 3 | AI11 (-) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 4 | AI4 (+) | DET_AMB_HUM_H2 | Ambient Humidity Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ambient Humidity Sensor - Humidity Sensor 2
Humidity Sensor | 16 | N/A | N/A | NI 9205 ADC | 6 | 4 | AI12 (-) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0+ | COOL_FLOW_R1_R3 | Coolant Flow Cable Assemblies | 21 | 4 |  | 12 | V450 | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R1-R3)
Coolant | 11 | R1-R3 | N/A | NI 9239 ADC | 5 | 0 | AI0- |  |  | 21 | 17 |  | 12 | V450 | J1 | 17 | CH 3-
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1+ | COOL_FLOW_R4 | Coolant Flow Cable Assemblies | 21 | 5 |  | 12 | V450 | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter (for R4)
Coolant | 12 | R4 | N/A | NI 9239 ADC | 5 | 1 | AI1- |  |  | 21 | 18 |  | 12 | V450 | J1 | 18 | CH 4-
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2+ | COOL_TEMP | Coolant Temperature Cable Assemblies | 21 | 2 |  | 12 | V450 | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant | 13 | N/A | N/A | NI 9239 ADC | 5 | 2 | AI2- |  |  | 21 | 15 |  | 12 | V450 | J1 | 15 | CH 1-
Coolant | 17 | N/A | N/A | NI 9239 ADC | 5 | 3 | AI3+ | COOL_LEAK_1 | Coolant Leak Detection - Type 1 - Outputs Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Coolant Leak Signal #1
Coolant | 17 | N/A | N/A | NI 9239 ADC | 5 | 3 | AI3- |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 19 |  |  | NI 9485 Relay | 8 | 0 | CH0a | Mpod_CRATE_1_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 1 Enable (+5V for enable)
Mpod Crate Enable | 19 |  |  | NI 9485 Relay | 8 | 0 | CH0b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 20 |  |  | NI 9485 Relay | 8 | 1 | CH1a | Mpod_CRATE_2_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 2 Enable (+5V for enable)
Mpod Crate Enable | 20 |  |  | NI 9485 Relay | 8 | 1 | CH1b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 21 |  |  | NI 9485 Relay | 8 | 2 | CH2a | Mpod_CRATE_3_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 3 Enable (+5V for enable)
Mpod Crate Enable | 21 |  |  | NI 9485 Relay | 8 | 2 | CH2b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 22 |  |  | NI 9485 Relay | 8 | 3 | CH3a | Mpod_CRATE_4_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 4 Enable (+5V for enable)
Mpod Crate Enable | 22 |  |  | NI 9485 Relay | 8 | 3 | CH3b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mpod Crate Enable | 23 |  |  | NI 9485 Relay | 8 | 4 | CH4a | Mpod_CRATE_5_ENA | Mpod Crate Enable Cable Assemblies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Mpod Crate # 5 Enable (+5V for enable)
Mpod Crate Enable | 23 |  |  | NI 9485 Relay | 8 | 4 | CH4b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 24 | N/A | N/A | NI 9485 Relay | 8 | 5 | CH5a | CHILLER_ENABLE | Chiller Disable Cable Assembly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 24V for BiRA Power Module via cRio Relay for chiller power
Coolant | 24 | N/A | N/A | NI 9485 Relay | 8 | 5 | CH5b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Coolant | 25 | N/A | N/A | NI 9485 Relay | 8 | 6 | CH6a | COOL_LEAK_RESET | Coolant Leak Detection - Type 4 - Reset Cable Assembly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Reset for Leak Controller
Coolant | 25 | N/A | N/A | NI 9485 Relay | 8 | 6 | CH6b |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## EPICS Slow Control Signals
SVT Slow Control Connections / Signals - By Patch Panel Blocks | [11 empty] | New Signals on 5/20/2015
2015-05-20
Category | SVT Region | SVT Sector/Module | Patch panel Block Type | Patch Panel Block Number | Block Pin # | SC Cable ID | VME Slot # | VME Board Type | Board Serial # | Vme Base Address | Vme Board Configuration | VME Board Connector | VME Connector Pin # | VME Board Signal Name | EPICS Signal Name | Comments
HFCB Temp | 1 | 1 | DB25 | 1 | 1 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S1T_Slot2 | SVT - HFCB Temp R1 M1 Top
HFCB Temp | 1 | 1 | DB25 | 1 | 14 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 1 | 1 | DB25 | 1 | 2 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R1S1B_Slot2 | SVT - HFCB Temp R1 M1 Bottom
HFCB Temp | 1 | 1 | DB25 | 1 | 15 | HFCB_R1_M1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 1 | 2 | DB25 | 1 | 3 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R1S2T_Slot2 | SVT - HFCB Temp R1 M2 Top
HFCB Temp | 1 | 2 | DB25 | 1 | 16 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 1 | 2 | DB25 | 1 | 4 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R1S2B_Slot2 | SVT - HFCB Temp R1 M2 Bottom
HFCB Temp | 1 | 2 | DB25 | 1 | 17 | HFCB_R1_M2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 1 | 3 | DB25 | 1 | 5 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R1S3T_Slot2 | SVT - HFCB Temp R1 M3 Top
HFCB Temp | 1 | 3 | DB25 | 1 | 18 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 1 | 3 | DB25 | 1 | 6 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R1S3B_Slot2 | SVT - HFCB Temp R1 M3 Bottom
HFCB Temp | 1 | 3 | DB25 | 1 | 19 | HFCB_R1_M3 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 1 | 4 | DB25 | 1 | 7 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R1S4T_Slot2 | SVT - HFCB Temp R1 M4 Top
HFCB Temp | 1 | 4 | DB25 | 1 | 20 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 1 | 4 | DB25 | 1 | 8 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R1S4B_Slot2 | SVT - HFCB Temp R1 M4 Bottom
HFCB Temp | 1 | 4 | DB25 | 1 | 21 | HFCB_R1_M4 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 1 | 9 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB1_T1_SL2 | Detector Environmental Temperature Sensor Board 1 - Temp Sensor 1
RTD Temp |  |  | DB25 | 1 | 22 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 1 | 10 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 1 | 23 | RTD_B1_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 1 | 11 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB1_T2_SL2 | Detector Environmental Temperature Sensor Board 1 - Temp Sensor 2
RTD Temp |  |  | DB25 | 1 | 24 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 1 | 12 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 1 | 25 | RTD_B1_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 1 | 5 | DB25 | 2 | 1 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R1S5T_Slot2 | SVT - HFCB Temp R1 M5 Top
HFCB Temp | 1 | 5 | DB25 | 2 | 14 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 1 | 5 | DB25 | 2 | 2 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R1S5B_Slot2 | SVT - HFCB Temp R1 M5 Bottom
HFCB Temp | 1 | 5 | DB25 | 2 | 15 | HFCB_R1_M5 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 1 | 6 | DB25 | 2 | 3 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R1S6T_Slot2 | SVT - HFCB Temp R1 M6 Top
HFCB Temp | 1 | 6 | DB25 | 2 | 16 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 1 | 6 | DB25 | 2 | 4 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R1S6B_Slot2 | SVT - HFCB Temp R1 M6 Bottom
HFCB Temp | 1 | 6 | DB25 | 2 | 17 | HFCB_R1_M6 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 1 | 7 | DB25 | 2 | 5 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R1S7T_Slot2 | SVT - HFCB Temp R1 M7 Top
HFCB Temp | 1 | 7 | DB25 | 2 | 18 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 1 | 7 | DB25 | 2 | 6 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R1S7B_Slot2 | SVT - HFCB Temp R1 M7 Bottom
HFCB Temp | 1 | 7 | DB25 | 2 | 19 | HFCB_R1_M7 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 1 | 8 | DB25 | 2 | 7 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R1S8T_Slot2 | SVT - HFCB Temp R1 M8 Top
HFCB Temp | 1 | 8 | DB25 | 2 | 20 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 1 | 8 | DB25 | 2 | 8 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R1S8B_Slot2 | SVT - HFCB Temp R1 M8 Bottom
HFCB Temp | 1 | 8 | DB25 | 2 | 21 | HFCB_R1_M8 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 2 | 9 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB2_T1_SL2 | Detector Environmental Temperature Sensor Board 2 - Temp Sensor 1
RTD Temp |  |  | DB25 | 2 | 22 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 2 | 10 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 2 | 23 | RTD_B2_T1 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 2 | 11 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB2_T2_SL2 | Detector Environmental Temperature Sensor Board 2 - Temp Sensor 2
RTD Temp |  |  | DB25 | 2 | 24 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 2 | 12 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 2 | 25 | RTD_B2_T2 | 2 | V450 | 120 | C000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 1 | 9 | DB25 | 3 | 1 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R1S9T_Slot3 | SVT - HFCB Temp R1 M9 Top
HFCB Temp | 1 | 9 | DB25 | 3 | 14 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 1 | 9 | DB25 | 3 | 2 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R1S9B_Slot3 | SVT - HFCB Temp R1 M9 Bottom
HFCB Temp | 1 | 9 | DB25 | 3 | 15 | HFCB_R1_M9 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 1 | 10 | DB25 | 3 | 3 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R1S10T_Slot3 | SVT - HFCB Temp R1 M10 Top
HFCB Temp | 1 | 10 | DB25 | 3 | 16 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 1 | 10 | DB25 | 3 | 4 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R1S10B_Slot3 | SVT - HFCB Temp R1 M10 Bottom
HFCB Temp | 1 | 10 | DB25 | 3 | 17 | HFCB_R1_M10 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 2 | 1 | DB25 | 3 | 5 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S1T_Slot3 | SVT - HFCB Temp R2 M1 Top
HFCB Temp | 2 | 1 | DB25 | 3 | 18 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 2 | 1 | DB25 | 3 | 6 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R2S1B_Slot3 | SVT - HFCB Temp R2 M1 Bottom
HFCB Temp | 2 | 1 | DB25 | 3 | 19 | HFCB_R2_M1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 2 | 2 | DB25 | 3 | 7 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R2S2T_Slot3 | SVT - HFCB Temp R2 M2 Top
HFCB Temp | 2 | 2 | DB25 | 3 | 20 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 2 | 2 | DB25 | 3 | 8 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R2S2B_Slot3 | SVT - HFCB Temp R2 M2 Bottom
HFCB Temp | 2 | 2 | DB25 | 3 | 21 | HFCB_R2_M2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 3 | 9 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB3_T1 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 1
RTD Temp |  |  | DB25 | 3 | 22 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 3 | 10 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 3 | 23 | RTD_B3_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 3 | 11 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB3_T2 | Detector Environmental Temperature Sensor Board 3 - Temp Sensor 2
RTD Temp |  |  | DB25 | 3 | 24 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 3 | 12 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 3 | 25 | RTD_B3_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 2 | 3 | DB25 | 4 | 1 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R2S3T_Slot3 | SVT - HFCB Temp R2 M3 Top
HFCB Temp | 2 | 3 | DB25 | 4 | 14 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 2 | 3 | DB25 | 4 | 2 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R2S3B_Slot3 | SVT - HFCB Temp R2 M3 Bottom
HFCB Temp | 2 | 3 | DB25 | 4 | 15 | HFCB_R2_M3 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 2 | 4 | DB25 | 4 | 3 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R2S4T_Slot3 | SVT - HFCB Temp R2 M4 Top
HFCB Temp | 2 | 4 | DB25 | 4 | 16 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 2 | 4 | DB25 | 4 | 4 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R2S4B_Slot3 | SVT - HFCB Temp R2 M4 Bottom
HFCB Temp | 2 | 4 | DB25 | 4 | 17 | HFCB_R2_M4 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 2 | 5 | DB25 | 4 | 5 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R2S5T_Slot3 | SVT - HFCB Temp R2 M5 Top
HFCB Temp | 2 | 5 | DB25 | 4 | 18 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 2 | 5 | DB25 | 4 | 6 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R2S5B_Slot3 | SVT - HFCB Temp R2 M5 Bottom
HFCB Temp | 2 | 5 | DB25 | 4 | 19 | HFCB_R2_M5 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 2 | 6 | DB25 | 4 | 7 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R2S6T_Slot3 | SVT - HFCB Temp R2 M6 Top
HFCB Temp | 2 | 6 | DB25 | 4 | 20 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 2 | 6 | DB25 | 4 | 8 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R2S6B_Slot3 | SVT - HFCB Temp R2 M6 Bottom
HFCB Temp | 2 | 6 | DB25 | 4 | 21 | HFCB_R2_M6 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 4 | 9 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB4_T1_SL3 | Detector Environmental Temperature Sensor Board 4 - Temp Sensor 1
RTD Temp |  |  | DB25 | 4 | 22 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 4 | 10 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 4 | 23 | RTD_B4_T1 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 4 | 11 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB4_T2_SL3 | Detector Environmental Temperature Sensor Board 4 - Temp Sensor 2
RTD Temp |  |  | DB25 | 4 | 24 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 4 | 12 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 4 | 25 | RTD_B4_T2 | 3 | V450 | 132 | D000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 2 | 7 | DB25 | 5 | 1 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R2S7T_Slot4 | SVT - HFCB Temp R2 M7 Top
HFCB Temp | 2 | 7 | DB25 | 5 | 14 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 2 | 7 | DB25 | 5 | 2 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R2S7B_Slot4 | SVT - HFCB Temp R2 M7 Bottom
HFCB Temp | 2 | 7 | DB25 | 5 | 15 | HFCB_R2_M7 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 2 | 8 | DB25 | 5 | 3 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R2S8T_Slot4 | SVT - HFCB Temp R2 M8 Top
HFCB Temp | 2 | 8 | DB25 | 5 | 16 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 2 | 8 | DB25 | 5 | 4 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R2S8B_Slot4 | SVT - HFCB Temp R2 M8 Bottom
HFCB Temp | 2 | 8 | DB25 | 5 | 17 | HFCB_R2_M8 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 2 | 9 | DB25 | 5 | 5 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R2S9T_Slot4 | SVT - HFCB Temp R2 M9 Top
HFCB Temp | 2 | 9 | DB25 | 5 | 18 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 2 | 9 | DB25 | 5 | 6 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R2S9B_Slot4 | SVT - HFCB Temp R2 M9 Bottom
HFCB Temp | 2 | 9 | DB25 | 5 | 19 | HFCB_R2_M9 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 2 | 10 | DB25 | 5 | 7 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R2S10T_Slot4 | SVT - HFCB Temp R2 M10 Top
HFCB Temp | 2 | 10 | DB25 | 5 | 20 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 2 | 10 | DB25 | 5 | 8 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R2S10B_Slot4 | SVT - HFCB Temp R2 M10 Bottom
HFCB Temp | 2 | 10 | DB25 | 5 | 21 | HFCB_R2_M10 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 5 | 9 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB5_T1_SL4 | Detector Environmental Temperature Sensor Board 5 - Temp Sensor 1
RTD Temp |  |  | DB25 | 5 | 22 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 5 | 10 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 5 | 23 | RTD_B5_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 5 | 11 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB5_T2_SL4 | Detector Environmental Temperature Sensor Board 5 - Temp Sensor 2
RTD Temp |  |  | DB25 | 5 | 24 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 5 | 12 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 5 | 25 | RTD_B5_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 2 | 11 | DB25 | 6 | 1 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R2S11T_Slot4 | SVT - HFCB Temp R2 M11 Top
HFCB Temp | 2 | 11 | DB25 | 6 | 14 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 2 | 11 | DB25 | 6 | 2 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R2S11B_Slot4 | SVT - HFCB Temp R2 M11 Bottom
HFCB Temp | 2 | 11 | DB25 | 6 | 15 | HFCB_R2_M11 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 2 | 12 | DB25 | 6 | 3 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R2S12T_Slot4 | SVT - HFCB Temp R2 M12 Top
HFCB Temp | 2 | 12 | DB25 | 6 | 16 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 2 | 12 | DB25 | 6 | 4 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R2S12B_Slot4 | SVT - HFCB Temp R2 M12 Bottom
HFCB Temp | 2 | 12 | DB25 | 6 | 17 | HFCB_R2_M12 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 2 | 13 | DB25 | 6 | 5 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R2S13T_Slot4 | SVT - HFCB Temp R2 M13 Top
HFCB Temp | 2 | 13 | DB25 | 6 | 18 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 2 | 13 | DB25 | 6 | 6 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R2S13B_Slot4 | SVT - HFCB Temp R2 M13 Bottom
HFCB Temp | 2 | 13 | DB25 | 6 | 19 | HFCB_R2_M13 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 2 | 14 | DB25 | 6 | 7 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R2S14T_Slot4 | SVT - HFCB Temp R2 M14 Top
HFCB Temp | 2 | 14 | DB25 | 6 | 20 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 2 | 14 | DB25 | 6 | 8 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R2S14B_Slot4 | SVT - HFCB Temp R2 M14 Bottom
HFCB Temp | 2 | 14 | DB25 | 6 | 21 | HFCB_R2_M14 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 6 | 9 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB6_T1_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 1
RTD Temp |  |  | DB25 | 6 | 22 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 6 | 10 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 6 | 23 | RTD_B6_T1 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 6 | 11 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB6_T2_SL4 | Detector Environmental Temperature Sensor Board 6- Temp Sensor 2
RTD Temp |  |  | DB25 | 6 | 24 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 6 | 12 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 6 | 25 | RTD_B6_T2 | 4 | V450 | 140 | E000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 1 | DB25 | 7 | 1 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S1T_Slot5 | SVT - HFCB Temp R3 M1 Top
HFCB Temp | 3 | 1 | DB25 | 7 | 14 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 1 | DB25 | 7 | 2 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S1B_Slot5 | SVT - HFCB Temp R3 M1 Bottom
HFCB Temp | 3 | 1 | DB25 | 7 | 15 | HFCB_R3_M1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 2 | DB25 | 7 | 3 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S2T_Slot5 | SVT - HFCB Temp R3 M2 Top
HFCB Temp | 3 | 2 | DB25 | 7 | 16 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 2 | DB25 | 7 | 4 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S2B_Slot5 | SVT - HFCB Temp R3 M2 Bottom
HFCB Temp | 3 | 2 | DB25 | 7 | 17 | HFCB_R3_M2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 3 | 3 | DB25 | 7 | 5 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R3S3T_Slot5 | SVT - HFCB Temp R3 M3 Top
HFCB Temp | 3 | 3 | DB25 | 7 | 18 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 3 | 3 | DB25 | 7 | 6 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R3S3B_Slot5 | SVT - HFCB Temp R3 M3 Bottom
HFCB Temp | 3 | 3 | DB25 | 7 | 19 | HFCB_R3_M3 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 3 | 4 | DB25 | 7 | 7 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R3S4T_Slot5 | SVT - HFCB Temp R3 M4 Top
HFCB Temp | 3 | 4 | DB25 | 7 | 20 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 3 | 4 | DB25 | 7 | 8 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R3S4B_Slot5 | SVT - HFCB Temp R3 M4 Bottom
HFCB Temp | 3 | 4 | DB25 | 7 | 21 | HFCB_R3_M4 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp | 4 |  | DB25 | 7 | 9 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB7_T1_SL5 | Detector Environmental Temperature Sensor Board 7- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 7 | 22 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp | 4 |  | DB25 | 7 | 10 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp | 4 |  | DB25 | 7 | 23 | RTD_B7_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp | 4 |  | DB25 | 7 | 11 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB7_T2_SL5 | Detector Environmental Temperature Sensor Board 7- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 7 | 24 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp | 4 |  | DB25 | 7 | 12 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp | 4 |  | DB25 | 7 | 25 | RTD_B7_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 3 | 5 | DB25 | 8 | 1 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R3S5T_Slot5 | SVT - HFCB Temp R3 M5 Top
HFCB Temp | 3 | 5 | DB25 | 8 | 14 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 3 | 5 | DB25 | 8 | 2 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R3S5B_Slot5 | SVT - HFCB Temp R3 M5 Bottom
HFCB Temp | 3 | 5 | DB25 | 8 | 15 | HFCB_R3_M5 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 3 | 6 | DB25 | 8 | 3 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R3S6T_Slot5 | SVT - HFCB Temp R3 M6 Top
HFCB Temp | 3 | 6 | DB25 | 8 | 16 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 3 | 6 | DB25 | 8 | 4 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R3S6B_Slot5 | SVT - HFCB Temp R3 M6 Bottom
HFCB Temp | 3 | 6 | DB25 | 8 | 17 | HFCB_R3_M6 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 3 | 7 | DB25 | 8 | 5 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R3S7T_Slot5 | SVT - HFCB Temp R3 M7 Top
HFCB Temp | 3 | 7 | DB25 | 8 | 18 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 3 | 7 | DB25 | 8 | 6 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R3S7B_Slot5 | SVT - HFCB Temp R3 M7 Bottom
HFCB Temp | 3 | 7 | DB25 | 8 | 19 | HFCB_R3_M7 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 3 | 8 | DB25 | 8 | 7 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R3S8T_Slot5 | SVT - HFCB Temp R3 M8 Top
HFCB Temp | 3 | 8 | DB25 | 8 | 20 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 3 | 8 | DB25 | 8 | 8 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R3S8B_Slot5 | SVT - HFCB Temp R3 M8 Bottom
HFCB Temp | 3 | 8 | DB25 | 8 | 21 | HFCB_R3_M8 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp | 4 |  | DB25 | 8 | 9 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB8_T1_SL5 | Detector Environmental Temperature Sensor Board 8- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 8 | 22 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp | 4 |  | DB25 | 8 | 10 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp | 4 |  | DB25 | 8 | 23 | RTD_B8_T1 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp | 4 |  | DB25 | 8 | 11 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB8_T2_SL5 | Detector Environmental Temperature Sensor Board 8- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 8 | 24 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp | 4 |  | DB25 | 8 | 12 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp | 4 |  | DB25 | 8 | 25 | RTD_B8_T2 | 5 | V450 | 141 | F000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 9 | DB25 | 9 | 1 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S9T_Slot6 | SVT - HFCB Temp R3 M9 Top
HFCB Temp | 3 | 9 | DB25 | 9 | 14 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 9 | DB25 | 9 | 2 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S9B_Slot6 | SVT - HFCB Temp R3 M9 Bottom
HFCB Temp | 3 | 9 | DB25 | 9 | 15 | HFCB_R3_M9 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 10 | DB25 | 9 | 3 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S10T_Slot6 | SVT - HFCB Temp R3 M10 Top
HFCB Temp | 3 | 10 | DB25 | 9 | 16 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 10 | DB25 | 9 | 4 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S10B_Slot6 | SVT - HFCB Temp R3 M10 Bottom
HFCB Temp | 3 | 10 | DB25 | 9 | 17 | HFCB_R3_M10 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 3 | 11 | DB25 | 9 | 5 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R3S11T_Slot6 | SVT - HFCB Temp R3 M11 Top
HFCB Temp | 3 | 11 | DB25 | 9 | 18 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 3 | 11 | DB25 | 9 | 6 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R3S11B_Slot6 | SVT - HFCB Temp R3 M11 Bottom
HFCB Temp | 3 | 11 | DB25 | 9 | 19 | HFCB_R3_M11 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 3 | 12 | DB25 | 9 | 7 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R3S12T_Slot6 | SVT - HFCB Temp R3 M12 Top
HFCB Temp | 3 | 12 | DB25 | 9 | 20 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 3 | 12 | DB25 | 9 | 8 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R3S12B_Slot6 | SVT - HFCB Temp R3 M12 Bottom
HFCB Temp | 3 | 12 | DB25 | 9 | 21 | HFCB_R3_M12 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp | 4 |  | DB25 | 9 | 9 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_ENV_TEMP_SB9_T1_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 9 | 22 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp | 4 |  | DB25 | 9 | 10 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp | 4 |  | DB25 | 9 | 23 | RTD_B9_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp | 4 |  | DB25 | 9 | 11 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_ENV_TEMP_SB9_T2_SL6 | Detector Environmental Temperature Sensor Board 9- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 9 | 24 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp | 4 |  | DB25 | 9 | 12 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp | 4 |  | DB25 | 9 | 25 | RTD_B9_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 3 | 13 | DB25 | 10 | 1 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R3S13T_Slot6 | SVT - HFCB Temp R3 M13 Top
HFCB Temp | 3 | 13 | DB25 | 10 | 14 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 3 | 13 | DB25 | 10 | 2 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R3S13B_Slot6 | SVT - HFCB Temp R3 M13 Bottom
HFCB Temp | 3 | 13 | DB25 | 10 | 15 | HFCB_R3_M13 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 3 | 14 | DB25 | 10 | 3 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R3S14T_Slot6 | SVT - HFCB Temp R3 M14 Top
HFCB Temp | 3 | 14 | DB25 | 10 | 16 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 3 | 14 | DB25 | 10 | 4 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R3S14B_Slot6 | SVT - HFCB Temp R3 M14 Bottom
HFCB Temp | 3 | 14 | DB25 | 10 | 17 | HFCB_R3_M14 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 3 | 15 | DB25 | 10 | 5 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R3S15T_Slot6 | SVT - HFCB Temp R3 M15 Top
HFCB Temp | 3 | 15 | DB25 | 10 | 18 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 3 | 15 | DB25 | 10 | 6 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R3S15B_Slot6 | SVT - HFCB Temp R3 M15 Bottom
HFCB Temp | 3 | 15 | DB25 | 10 | 19 | HFCB_R3_M15 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 3 | 16 | DB25 | 10 | 7 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R3S16T_Slot6 | SVT - HFCB Temp R3 M16 Top
HFCB Temp | 3 | 16 | DB25 | 10 | 20 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 3 | 16 | DB25 | 10 | 8 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R3S16B_Slot6 | SVT - HFCB Temp R3 M16 Bottom
HFCB Temp | 3 | 16 | DB25 | 10 | 21 | HFCB_R3_M16 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp | 4 |  | DB25 | 10 | 9 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_ENV_TEMP_SB10_T1_SL6 | Detector Environmental Temperature Sensor Board 10- Temp Sensor 1
RTD Temp | 4 |  | DB25 | 10 | 22 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp | 4 |  | DB25 | 10 | 10 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp | 4 |  | DB25 | 10 | 23 | RTD_B10_T1 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp | 4 |  | DB25 | 10 | 11 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_ENV_TEMP_SB10_T2_SL6 | Detector Environmental Temperature Sensor Board 10- Temp Sensor 2
RTD Temp | 4 |  | DB25 | 10 | 24 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp | 4 |  | DB25 | 10 | 12 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp | 4 |  | DB25 | 10 | 25 | RTD_B10_T2 | 6 | V450 | 142 | 10000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 3 | 17 | DB25 | 11 | 1 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R3S17T_Slot7 | SVT - HFCB Temp R3 M17 Top
HFCB Temp | 3 | 17 | DB25 | 11 | 14 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 3 | 17 | DB25 | 11 | 2 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R3S17B_Slot7 | SVT - HFCB Temp R3 M17 Bottom
HFCB Temp | 3 | 17 | DB25 | 11 | 15 | HFCB_R3_M17 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 3 | 18 | DB25 | 11 | 3 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R3S18T_Slot7 | SVT - HFCB Temp R3 M18 Top
HFCB Temp | 3 | 18 | DB25 | 11 | 16 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 3 | 18 | DB25 | 11 | 4 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R3S18B_Slot7 | SVT - HFCB Temp R3 M18 Bottom
HFCB Temp | 3 | 18 | DB25 | 11 | 17 | HFCB_R3_M18 | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
|  |  | DB25 | 11 | 5 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+
|  |  | DB25 | 11 | 18 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
|  |  | DB25 | 11 | 6 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+
|  |  | DB25 | 11 | 19 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
|  |  | DB25 | 11 | 7 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+
|  |  | DB25 | 11 | 20 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
|  |  | DB25 | 11 | 8 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+
|  |  |  | 11 | 21 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 11 | 9 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 11 | 22 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 11 | 10 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 11 | 23 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 11 | 11 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 11 | 24 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 11 | 12 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 11 | 25 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
|  |  | DB25 | 12 | 1 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+
|  |  | DB25 | 12 | 14 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
|  |  | DB25 | 12 | 2 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+
|  |  | DB25 | 12 | 15 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
|  |  | DB25 | 12 | 3 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+
|  |  | DB25 | 12 | 16 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
|  |  | DB25 | 12 | 4 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+
|  |  | DB25 | 12 | 17 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
|  |  | DB25 | 12 | 5 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+
|  |  | DB25 | 12 | 18 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
|  |  | DB25 | 12 | 6 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+
|  |  | DB25 | 12 | 19 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
|  |  | DB25 | 12 | 7 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+
|  |  | DB25 | 12 | 20 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
|  |  | DB25 | 12 | 8 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+
|  |  | DB25 | 12 | 21 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 12 | 9 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 12 | 22 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 12 | 10 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 12 | 23 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 12 | 11 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 12 | 24 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 12 | 12 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 12 | 25 |  | 7 | V450 | 143 | 11000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
HFCB Temp | 4 | 1 | DB25 | 13 | 1 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S1T_Slot8 | SVT - HFCB Temp R4 M1 Top
HFCB Temp | 4 | 1 | DB25 | 13 | 14 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 1 | DB25 | 13 | 2 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S1B_Slot8 | SVT - HFCB Temp R4 M1 Bottom
HFCB Temp | 4 | 1 | DB25 | 13 | 15 | HFCB_R4_M1 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 2 | DB25 | 13 | 3 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S2T_Slot8 | SVT - HFCB Temp R4 M2 Top
HFCB Temp | 4 | 2 | DB25 | 13 | 16 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 2 | DB25 | 13 | 4 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S2B_Slot8 | SVT - HFCB Temp R4 M2 Bottom
HFCB Temp | 4 | 2 | DB25 | 13 | 17 | HFCB_R4_M2 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 3 | DB25 | 13 | 5 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S3T_Slot8 | SVT - HFCB Temp R4 M3 Top
HFCB Temp | 4 | 3 | DB25 | 13 | 18 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 3 | DB25 | 13 | 6 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S3B_Slot8 | SVT - HFCB Temp R4 M3 Bottom
HFCB Temp | 4 | 3 | DB25 | 13 | 19 | HFCB_R4_M3 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 4 | DB25 | 13 | 7 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S4T_Slot8 | SVT - HFCB Temp R4 M4 Top
HFCB Temp | 4 | 4 | DB25 | 13 | 20 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 4 | DB25 | 13 | 8 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S4B_Slot8 | SVT - HFCB Temp R4 M4 Bottom
HFCB Temp | 4 | 4 | DB25 | 13 | 21 | HFCB_R4_M4 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 13 | 9 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 13 | 22 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 13 | 10 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 13 | 23 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 13 | 11 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 13 | 24 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 13 | 12 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 13 | 25 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 5 | DB25 | 14 | 1 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S5T_Slot8 | SVT - HFCB Temp R4 M5 Top
HFCB Temp | 4 | 5 | DB25 | 14 | 14 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 5 | DB25 | 14 | 2 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S5B_Slot8 | SVT - HFCB Temp R4 M5 Bottom
HFCB Temp | 4 | 5 | DB25 | 14 | 15 | HFCB_R4_M5 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 6 | DB25 | 14 | 3 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S6T_Slot8 | SVT - HFCB Temp R4 M6 Top
HFCB Temp | 4 | 6 | DB25 | 14 | 16 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 6 | DB25 | 14 | 4 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S6B_Slot8 | SVT - HFCB Temp R4 M6 Bottom
HFCB Temp | 4 | 6 | DB25 | 14 | 17 | HFCB_R4_M6 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 7 | DB25 | 14 | 5 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S7T_Slot8 | SVT - HFCB Temp R4 M7 Top
HFCB Temp | 4 | 7 | DB25 | 14 | 18 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 7 | DB25 | 14 | 6 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S7B_Slot8 | SVT - HFCB Temp R4 M7 Bottom
HFCB Temp | 4 | 7 | DB25 | 14 | 19 | HFCB_R4_M7 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 8 | DB25 | 14 | 7 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S8T_Slot8 | SVT - HFCB Temp R4 M8 Top
HFCB Temp | 4 | 8 | DB25 | 14 | 20 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 8 | DB25 | 14 | 8 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S8B_Slot8 | SVT - HFCB Temp R4 M8 Bottom
HFCB Temp | 4 | 8 | DB25 | 14 | 21 | HFCB_R4_M8 | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 14 | 9 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 14 | 22 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 14 | 10 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 14 | 23 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 14 | 11 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 14 | 24 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 14 | 12 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 14 | 25 |  | 8 | V450 | 144 | 12000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdB S-
HFCB Temp | 4 | 9 | DB25 | 15 | 1 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S9T_Slot9 | SVT - HFCB Temp R4 M9 Top
HFCB Temp | 4 | 9 | DB25 | 15 | 14 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 9 | DB25 | 15 | 2 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S9B_Slot9 | SVT - HFCB Temp R4 M9 Bottom
HFCB Temp | 4 | 9 | DB25 | 15 | 15 | HFCB_R4_M9 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 10 | DB25 | 15 | 3 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S10T_Slot9 | SVT - HFCB Temp R4 M10 Top
HFCB Temp | 4 | 10 | DB25 | 15 | 16 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 10 | DB25 | 15 | 4 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S10B_Slot9 | SVT - HFCB Temp R4 M10 Bottom
HFCB Temp | 4 | 10 | DB25 | 15 | 17 | HFCB_R4_M10 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 11 | DB25 | 15 | 5 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S11T_Slot9 | SVT - HFCB Temp R4 M11 Top
HFCB Temp | 4 | 11 | DB25 | 15 | 18 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 11 | DB25 | 15 | 6 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S11B_Slot9 | SVT - HFCB Temp R4 M11 Bottom
HFCB Temp | 4 | 11 | DB25 | 15 | 19 | HFCB_R4_M11 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 12 | DB25 | 15 | 7 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S12T_Slot9 | SVT - HFCB Temp R4 M12 Top
HFCB Temp | 4 | 12 | DB25 | 15 | 20 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 12 | DB25 | 15 | 8 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S12B_Slot9 | SVT - HFCB Temp R4 M12 Bottom
HFCB Temp | 4 | 12 | DB25 | 15 | 21 | HFCB_R4_M12 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 15 | 9 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 15 | 22 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 15 | 10 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 15 | 23 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 15 | 11 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 15 | 24 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 15 | 12 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 15 | 25 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 13 | DB25 | 16 | 1 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S13T_Slot9 | SVT - HFCB Temp R4 M13 Top
HFCB Temp | 4 | 13 | DB25 | 16 | 14 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 13 | DB25 | 16 | 2 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S13B_Slot9 | SVT - HFCB Temp R4 M13 Bottom
HFCB Temp | 4 | 13 | DB25 | 16 | 15 | HFCB_R4_M13 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 14 | DB25 | 16 | 3 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S14T_Slot9 | SVT - HFCB Temp R4 M14 Top
HFCB Temp | 4 | 14 | DB25 | 16 | 16 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 14 | DB25 | 16 | 4 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S14B_Slot9 | SVT - HFCB Temp R4 M14 Bottom
HFCB Temp | 4 | 14 | DB25 | 16 | 17 | HFCB_R4_M14 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 15 | DB25 | 16 | 5 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S15T_Slot9 | SVT - HFCB Temp R4 M15 Top
HFCB Temp | 4 | 15 | DB25 | 16 | 18 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 15 | DB25 | 16 | 6 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S15B_Slot9 | SVT - HFCB Temp R4 M15 Bottom
HFCB Temp | 4 | 15 | DB25 | 16 | 19 | HFCB_R4_M15 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 16 | DB25 | 16 | 7 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S16T_Slot9 | SVT - HFCB Temp R4 M16 Top
HFCB Temp | 4 | 16 | DB25 | 16 | 20 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 16 | DB25 | 16 | 8 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S16B_Slot9 | SVT - HFCB Temp R4 M16 Bottom
HFCB Temp | 4 | 16 | DB25 | 16 | 21 | HFCB_R4_M16 | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 16 | 9 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 16 | 22 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 16 | 10 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 16 | 23 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 16 | 11 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 16 | 24 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 16 | 12 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 16 | 25 |  | 9 | V450 | 145 | 13000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdB S-
HFCB Temp | 4 | 17 | DB25 | 17 | 1 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_TEMP_R4S17T_Slot10 | SVT - HFCB Temp R4 M17 Top
HFCB Temp | 4 | 17 | DB25 | 17 | 14 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
HFCB Temp | 4 | 17 | DB25 | 17 | 2 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_TEMP_R4S17B_Slot10 | SVT - HFCB Temp R4 M17 Bottom
HFCB Temp | 4 | 17 | DB25 | 17 | 15 | HFCB_R4_M17 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
HFCB Temp | 4 | 18 | DB25 | 17 | 3 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_TEMP_R4S18T_Slot10 | SVT - HFCB Temp R4 M18 Top
HFCB Temp | 4 | 18 | DB25 | 17 | 16 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
HFCB Temp | 4 | 18 | DB25 | 17 | 4 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_TEMP_R4S18B_Slot10 | SVT - HFCB Temp R4 M18 Bottom
HFCB Temp | 4 | 18 | DB25 | 17 | 17 | HFCB_R4_M18 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
HFCB Temp | 4 | 19 | DB25 | 17 | 5 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_TEMP_R4S19T_Slot10 | SVT - HFCB Temp R4 M19 Top
HFCB Temp | 4 | 19 | DB25 | 17 | 18 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
HFCB Temp | 4 | 19 | DB25 | 17 | 6 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_TEMP_R4S19B_Slot10 | SVT - HFCB Temp R4 M19 Bottom
HFCB Temp | 4 | 19 | DB25 | 17 | 19 | HFCB_R4_M19 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
HFCB Temp | 4 | 20 | DB25 | 17 | 7 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_TEMP_R4S20T_Slot10 | SVT - HFCB Temp R4 M20 Top
HFCB Temp | 4 | 20 | DB25 | 17 | 20 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
HFCB Temp | 4 | 20 | DB25 | 17 | 8 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_TEMP_R4S20B_Slot10 | SVT - HFCB Temp R4 M20 Bottom
HFCB Temp | 4 | 20 | DB25 | 17 | 21 | HFCB_R4_M20 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 17 | 9 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 17 | 22 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 17 | 10 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 17 | 23 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 17 | 11 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 17 | 24 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 17 | 12 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 17 | 25 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
HFCB Temp | 4 | 21 | DB25 | 18 | 1 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_TEMP_R4S21T_Slot10 | SVT - HFCB Temp R4 M21 Top
HFCB Temp | 4 | 21 | DB25 | 18 | 14 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
HFCB Temp | 4 | 21 | DB25 | 18 | 2 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_TEMP_R4S21B_Slot10 | SVT - HFCB Temp R4 M21 Bottom
HFCB Temp | 4 | 21 | DB25 | 18 | 15 | HFCB_R4_M21 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
HFCB Temp | 4 | 22 | DB25 | 18 | 3 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_TEMP_R4S22T_Slot10 | SVT - HFCB Temp R4 M22 Top
HFCB Temp | 4 | 22 | DB25 | 18 | 16 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
HFCB Temp | 4 | 22 | DB25 | 18 | 4 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_TEMP_R4S22B_Slot10 | SVT - HFCB Temp R4 M22 Bottom
HFCB Temp | 4 | 22 | DB25 | 18 | 17 | HFCB_R4_M22 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
HFCB Temp | 4 | 23 | DB25 | 18 | 5 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_TEMP_R4S23T_Slot10 | SVT - HFCB Temp R4 M23 Top
HFCB Temp | 4 | 23 | DB25 | 18 | 18 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
HFCB Temp | 4 | 23 | DB25 | 18 | 6 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_TEMP_R4S23B_Slot10 | SVT - HFCB Temp R4 M23 Bottom
HFCB Temp | 4 | 23 | DB25 | 18 | 19 | HFCB_R4_M23 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
HFCB Temp | 4 | 24 | DB25 | 18 | 7 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_TEMP_R4S24T_Slot10 | SVT - HFCB Temp R4 M24 Top
HFCB Temp | 4 | 24 | DB25 | 18 | 20 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
HFCB Temp | 4 | 24 | DB25 | 18 | 8 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_TEMP_R4S24B_Slot10 | SVT - HFCB Temp R4 M24 Bottom
HFCB Temp | 4 | 24 | DB25 | 18 | 21 | HFCB_R4_M24 | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 18 | 9 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 18 | 22 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 18 | 10 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 18 | 23 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 18 | 11 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 18 | 24 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 18 | 12 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 18 | 25 |  | 10 | V450 | 146 | 14000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
Humidity Sensor |  |  | DB25 | 19 | 1 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_ENV_Hum_SB1_H1_SL11 | Detector Environmental Humidity Sensor Board 1 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 14 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
Humidity Sensor |  |  | DB25 | 19 | 2 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_ENV_Hum_SB1_H2_SL11 | Detector Environmental Humidity Sensor Board 1 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 15 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
Humidity Sensor |  |  | DB25 | 19 | 3 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_ENV_Hum_SB2_H1_SL11 | Detector Environmental Humidity Sensor Board 2 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 16 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
Humidity Sensor |  |  | DB25 | 19 | 4 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_ENV_Hum_SB2_H2_SL11 | Detector Environmental Humidity Sensor Board 2 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 17 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
Humidity Sensor |  |  | DB25 | 19 | 5 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_ENV_Hum_SB3_H1_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 18 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
Humidity Sensor |  |  | DB25 | 19 | 6 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+ | B_SVT_ENV_Hum_SB3_H2_SL11 | Detector Environmental Humidity Sensor Board 3 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 19 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
Humidity Sensor |  |  | DB25 | 19 | 7 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+ | B_SVT_ENV_Hum_SB4_H1_SL11 | Detector Environmental Humidity Sensor Board 4 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 19 | 20 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
Humidity Sensor |  |  | DB25 | 19 | 8 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+ | B_SVT_ENV_Hum_SB4_H2_SL11 | Detector Environmental Humidity Sensor Board 4 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 19 | 21 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 19 | 9 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+ | B_SVT_EX_ENV_TEMP_SB1_T1_SL11 | External Environmental Temperature Sensor Board 1- Temp Sensor 1
RTD Temp |  |  | DB25 | 19 | 22 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 19 | 10 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 19 | 23 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 19 | 11 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+ | B_SVT_EX_ENV_TEMP_SB1_T2_SL11 | External Environmental Temperature Sensor Board 1- Temp Sensor 2
RTD Temp |  |  | DB25 | 19 | 24 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 19 | 12 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 19 | 25 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
Humidity Sensor |  |  | DB25 | 20 | 1 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_ENV_Hum_SB5_H1_SL11 | Detector Environmental Humidity Sensor Board 5 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 14 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
Humidity Sensor |  |  | DB25 | 20 | 2 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_ENV_Hum_SB5_H2_SL11 | Detector Environmental Humidity Sensor Board 5 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 15 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
Humidity Sensor |  |  | DB25 | 20 | 3 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_ENV_Hum_SB6_H1_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 16 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
Humidity Sensor |  |  | DB25 | 20 | 4 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB6_H2_SL11 | Detector Environmental Humidity Sensor Board 6 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 17 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
Humidity Sensor |  |  | DB25 | 20 | 5 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_EX_ENV_Hum_SB1_H1_SL11 | External Environmental Humidity Sensor Board 1 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 18 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
Humidity Sensor |  |  | DB25 | 20 | 6 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_EX_ENV_Hum_SB1_H2_SL11 | External Environmental Humidity Sensor Board 1 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 19 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
Humidity Sensor |  |  | DB25 | 20 | 7 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_EX_ENV_Hum_SB2_H1_SL11 | External Environmental Humidity Sensor Board 2 - Humidity Sensor 1
Humidity Sensor |  |  | DB25 | 20 | 20 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
Humidity Sensor |  |  | DB25 | 20 | 8 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_EX_ENV_Hum_SB2_H2_SL11 | External Environmental Humidity Sensor Board 2 - Humidity Sensor 2
Humidity Sensor |  |  | DB25 | 20 | 21 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 20 | 9 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+ | B_SVT_EX_ENV_TEMP_SB2_T1_SL11 | External Environmental Temperature Sensor Board 2- Temp Sensor 1
RTD Temp |  |  | DB25 | 20 | 22 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 20 | 10 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 20 | 23 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 20 | 11 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+ | B_SVT_EX_ENV_TEMP_SB2_T2_SL11 | External Environmental Temperature Sensor Board 2- Temp Sensor 2
RTD Temp |  |  | DB25 | 20 | 24 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 20 | 12 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 20 | 25 |  | 11 | V450 | 147 | 15000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-
Coolant |  |  | DB25 | 21 | 1 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 1 | CH 0+ | B_SVT_Cool_Inlet_Flow | Inlet Coolant Flow Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 14 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 14 | CH 0-
Coolant |  |  | DB25 | 21 | 2 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 2 | CH 1+ | B_SVT_Cool_Inlet_Temp | Inlet Coolant Temperature Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 15 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 15 | CH 1-
Coolant |  |  | DB25 | 21 | 3 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 3 | CH 2+ | B_SVT_Cool_Inlet_Pres | Inlet Coolant Pressure Meter. Uses Florite controller and the Proteus Industries sensor assembly
Coolant |  |  | DB25 | 21 | 16 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 16 | CH 2-
Coolant |  |  | DB25 | 21 | 4 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 4 | CH 3+ | B_SVT_Cool_Outlet_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter
Coolant |  |  | DB25 | 21 | 17 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 17 | CH 3-
|  |  | DB25 | 21 | 5 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 5 | CH 4+ | B_SVT_R4_Cool_Flow | Outlet Coolant Flow Meter. Users Omega FLR6302D Flow Meter
|  |  | DB25 | 21 | 18 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 18 | CH 4-
|  |  | DB25 | 21 | 6 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 6 | CH 5+
|  |  | DB25 | 21 | 19 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 19 | CH 5-
|  |  | DB25 | 21 | 7 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 7 | CH 6+
|  |  | DB25 | 21 | 20 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 20 | CH 6-
|  |  | DB25 | 21 | 8 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 8 | CH 7+
|  |  | DB25 | 21 | 21 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 21 | CH 7-
RTD Temp |  |  | DB25 | 21 | 9 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 9 | RtdA E+
RTD Temp |  |  | DB25 | 21 | 22 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 22 | RtdA E-
RTD Temp |  |  | DB25 | 21 | 10 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 10 | RtdA S+
RTD Temp |  |  | DB25 | 21 | 23 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 23 | RtdA S-
RTD Temp |  |  | DB25 | 21 | 11 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 11 | RtdB E+
RTD Temp |  |  | DB25 | 21 | 24 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 24 | RtdB E-
RTD Temp |  |  | DB25 | 21 | 12 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 12 | RtdB S+
RTD Temp |  |  | DB25 | 21 | 25 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J1 | 25 | RtdB S-
Humidity Sensor | 4 |  | DB25 | 22 | 1 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 1 | CH 8+ | B_SVT_ENV_Hum_SB7_H1_SL12 | Detector Environmental Humidity Sensor Board 7 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 14 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 14 | CH 8-
Humidity Sensor | 4 |  | DB25 | 22 | 2 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 2 | CH 9+ | B_SVT_ENV_Hum_SB7_H2_SL12 | Detector Environmental Humidity Sensor Board 7 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 15 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 15 | CH 9-
Humidity Sensor | 4 |  | DB25 | 22 | 3 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 3 | CH 10+ | B_SVT_ENV_Hum_SB8_H1_SL12 | Detector Environmental Humidity Sensor Board 8- Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 16 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 16 | CH 10-
Humidity Sensor | 4 |  | DB25 | 22 | 4 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 4 | CH 11+ | B_SVT_ENV_Hum_SB8_H2_SL12 | Detector Environmental Humidity Sensor Board 8 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 17 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 17 | CH 11-
Humidity Sensor | 4 |  | DB25 | 22 | 5 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 5 | CH 12+ | B_SVT_ENV_Hum_SB9_H1_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 18 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 18 | CH 12-
Humidity Sensor | 4 |  | DB25 | 22 | 6 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 6 | CH 13+ | B_SVT_ENV_Hum_SB9_H2_SL12 | Detector Environmental Humidity Sensor Board 9 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 19 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 19 | CH 13-
Humidity Sensor | 4 |  | DB25 | 22 | 7 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 7 | CH 14+ | B_SVT_ENV_Hum_SB10_H1_SL12 | Detector Environmental Humidity Sensor Board 10 - Humidity Sensor 1
Humidity Sensor | 4 |  | DB25 | 22 | 20 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 20 | CH 14-
Humidity Sensor | 4 |  | DB25 | 22 | 8 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 8 | CH 15+ | B_SVT_ENV_Hum_SB10_H2_SL12 | Detector Environmental Humidity Sensor Board 10 - Humidity Sensor 2
Humidity Sensor | 4 |  | DB25 | 22 | 21 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 21 | CH 15-
RTD Temp |  |  | DB25 | 22 | 9 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 9 | RtdC E+
RTD Temp |  |  | DB25 | 22 | 22 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 22 | RtdC E-
RTD Temp |  |  | DB25 | 22 | 10 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 10 | RtdC S+
RTD Temp |  |  | DB25 | 22 | 23 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 23 | RtdC S-
RTD Temp |  |  | DB25 | 22 | 11 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 11 | RtdD E+
RTD Temp |  |  | DB25 | 22 | 24 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 24 | RtdD E-
RTD Temp |  |  | DB25 | 22 | 12 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 12 | RtdD S+
RTD Temp |  |  | DB25 | 22 | 25 |  | 12 | V450 | 148 | 16000 | +/-12V @ 4.17 Hz | J2 | 25 | RtdD S-

## SVT EPICS Interface
Hall B SVT Hardware Interlock System EPICS Interface
Signal Category | LabVIEW Signal Name | Access Type | Data Type | EPICS Client Process Variable (PV) | Units | PV # | Group # | LabVIEW .db Client file
Signal Monitoring | SVT EPICS HFCB Temp R1 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1 | °C | 1 | 1 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1"){}
| SVT EPICS HFCB Temp R2 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2 | °C | 2 | 2 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2"){}
| SVT EPICS HFCB Temp R3 M1 Top | Read Only | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3 | °C | 3 | 3 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3"){}
| SVT EPICS Detector Int Temp R2 | Read Only | Double | B_DET_SVT_INTLK_INT_TEMP_R2 | °C | 4 | 4 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2"){}
| SVT EPICS Detector Int Temp R3 | Read Only | Double | B_DET_SVT_INTLK_INT_TEMP_R3 | °C | 5 | 5 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3"){}
| SVT EPICS Ambient Temp 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_TEMP1 | °C | 6 | 6 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1"){}
| SVT EPICS Ambient Temp 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_TEMP2 | °C | 7 | 7 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2"){}
| SVT EPICS Det Internal Humidity R2 | Read Only | Double | B_DET_SVT_INTLK_INT_HUMID_R2 | %RH | 8 | 8 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2"){}
| SVT EPICS Det Internal Humidity R3 | Read Only | Double | B_DET_SVT_INTLK_INT_HUMID_R3 | %RH | 9 | 9 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3"){}
| SVT EPICS Det Internal Dew Point Alarm R2 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_ALM_R2 |  | 10 | 10 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_ALM_R2"){}
| SVT EPICS Det Internal Dew Point Alarm R3 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_ALM_R3 |  | 11 | 11 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_ALM_R3"){}
| SVT EPICS Ambient Humidity H1 | Read Only | Double | B_DET_SVT_INTLK_AMB_HUMID1 | %RH | 12 | 12 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1"){}
| SVT EPICS Ambient Humidity H2 | Read Only | Double | B_DET_SVT_INTLK_AMB_HUMID2 | %RH | 13 | 13 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2"){}
| SVT EPICS Ambient Dew Point Alarm 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP_ALM1 |  | 14 | 14 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP_ALM1"){}
| SVT EPICS Ambient Dew Point Alarm 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP_ALM2 |  | 15 | 15 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP_ALM2"){}
| SVT EPICS Outlet Coolant Flow | Read Only | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW | L/Min | 16 | 16 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW"){}
| SVT EPICS Inlet Coolant Flow | Read Only | Double | B_DET_SVT_INTLK_COOL_IN_FLOW | L/Min | 17 | 17 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW"){}
| SVT EPICS Coolant Temp | Read Only | Double | B_DET_SVT_INTLK_COOL_TEMP | °C | 18 | 18 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP"){}
| SVT EPICS Ambient Dew Point 1 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP1 |  | 19 | 19 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1"){}
| SVT EPICS Ambient Dew Point 2 | Read Only | Double | B_DET_SVT_INTLK_AMB_DEWP2 |  | 20 | 20 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2"){}
| SVT EPICS Det Internal Dew Point R2 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_R2 |  | 21 | 21 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2"){}
| SVT EPICS Det Internal Dew Point R3 | Read Only | Double | B_DET_SVT_INTLK_INT_DEWP_R3 |  | 22 | 22 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3"){}
Individual Sensor Interlock Status | SVT EPICS HFCB Temp R1 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_HI_STAT | N/A | 23 | 1 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_HI_STAT"){}
| SVT EPICS HFCB Temp R1 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LO_STAT | N/A | 24 | 2 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_LO_STAT"){}
| SVT EPICS HFCB Temp R2 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_HI_STAT | N/A | 25 | 3 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_HI_STAT"){}
| SVT EPICS HFCB Temp R2 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LO_STAT | N/A | 26 | 4 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_LO_STAT"){}
| SVT EPICS HFCB Temp R3 M1 Top Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_HI_STAT | N/A | 27 | 5 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_HI_STAT"){}
| SVT EPICS HFCB Temp R3 M1 Top Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LO_STAT | N/A | 28 | 6 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_LO_STAT"){}
| SVT EPICS Detector Int Temp R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_HI_STAT | N/A | 29 | 7 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_HI_STAT"){}
| SVT EPICS Detector Int Temp R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LO_STAT | N/A | 30 | 8 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_LO_STAT"){}
| SVT EPICS Detector Int Temp R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_HI_STAT | N/A | 31 | 9 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_HI_STAT"){}
| SVT EPICS Detector Int Temp R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LO_STAT | N/A | 32 | 10 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_LO_STAT"){}
| SVT EPICS Ambient Temp 1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_HI_STAT | N/A | 33 | 11 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_HI_STAT"){}
| SVT EPICS Ambient Temp 1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LO_STAT | N/A | 34 | 12 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_LO_STAT"){}
| SVT EPICS Ambient Temp 2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_HI_STAT | N/A | 35 | 13 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_HI_STAT"){}
| SVT EPICS Ambient Temp 2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LO_STAT | N/A | 36 | 14 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_LO_STAT"){}
| SVT EPICS Det Internal Humidity R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_HI_STAT | N/A | 37 | 15 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_HI_STAT"){}
| SVT EPICS Det Internal Humidity R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LO_STAT | N/A | 38 | 16 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_LO_STAT"){}
| SVT EPICS Det Internal Humidity R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_HI_STAT | N/A | 39 | 17 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_HI_STAT"){}
| SVT EPICS Det Internal Humidity R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LO_STAT | N/A | 40 | 18 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_LO_STAT"){}
| SVT EPICS Det Internal Dew Point R2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_HI_STAT | N/A | 41 | 19 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_HI_STAT"){}
| SVT EPICS Det Internal Dew Point R2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LO_STAT | N/A | 42 | 20 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_LO_STAT"){}
| SVT EPICS Det Internal Dew Point R3 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_HI_STAT | N/A | 43 | 21 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_HI_STAT"){}
| SVT EPICS Det Internal Dew Point R3 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LO_STAT | N/A | 44 | 22 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_LO_STAT"){}
| SVT EPICS Ambient Humidity H1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_HI_STAT | N/A | 45 | 23 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_HI_STAT"){}
| SVT EPICS Ambient Humidity H1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LO_STAT | N/A | 46 | 24 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_LO_STAT"){}
| SVT EPICS Ambient Humidity H2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_HI_STAT | N/A | 47 | 25 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_HI_STAT"){}
| SVT EPICS Ambient Humidity H2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LO_STAT | N/A | 48 | 26 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_LO_STAT"){}
| SVT EPICS Ambient Dew Point 1 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_HI_STAT | N/A | 49 | 27 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_HI_STAT"){}
| SVT EPICS Ambient Dew Point 1 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LO_STAT | N/A | 50 | 28 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_LO_STAT"){}
| SVT EPICS Ambient Dew Point 2 Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_HI_STAT | N/A | 51 | 29 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_HI_STAT"){}
| SVT EPICS Ambient Dew Point 2 Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LO_STAT | N/A | 52 | 30 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_LO_STAT"){}
| SVT EPICS Outlet Coolant Flow Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_HI_STAT | N/A | 53 | 31 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_HI_STAT"){}
| SVT EPICS Outlet Coolant Flow Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LO_STAT | N/A | 54 | 32 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_LO_STAT"){}
| SVT EPICS Inlet Coolant Flow Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_HI_STAT | N/A | 55 | 33 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_HI_STAT"){}
| SVT EPICS Inlet Coolant Flow Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LO_STAT | N/A | 56 | 34 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_LO_STAT"){}
| SVT EPICS Coolant Temp Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_HI_STAT | N/A | 57 | 35 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_HI_STAT"){}
| SVT EPICS Coolant Temp Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LO_STAT | N/A | 58 | 36 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_LO_STAT"){}
| SVT EPICS Coolant Leak Hi Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_HI_STAT | N/A | 59 | 37 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK_HI_STAT"){}
| SVT EPICS Coolant Leak Lo Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LO_STAT | N/A | 60 | 38 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK_LO_STAT"){}
Sum of Interlocks Status | SVT EPICS Any Interlock Over Limit? | Read Only | Boolean | B_DET_SVT_INTLK_ANY_OVERLIMIT | N/A | 61 | 1 | record (ai, "B_DET_SVT_INTLK_ANY_OVERLIMIT"){}
Sum of Temperature Status | SVT EPICS Temperature Status | Read Only | Boolean | B_DET_SVT_INTLK_TEMP_STATUS | N/A | 62 | 1 | record (ai, "B_DET_SVT_INTLK_TEMP_STATUS"){}
Sum of Humidity Status | SVT EPICS Humidity Status | Read Only | Boolean | B_DET_SVT_INTLK_HUMID_STATUS | N/A | 63 | 1 | record (ai, "B_DET_SVT_INTLK_HUMID_STATUS"){}
Sum of Dew Point Status | SVT EPICS Dew Point Status | Read Only | Boolean | B_DET_SVT_INTLK_DEWP_STATUS | N/A | 64 | 1 | record (ai, "B_DET_SVT_INTLK_DEWP_STATUS"){}
Sum of Coolant Inlet Flow Status | SVT EPICS Inlet Coolant Flow Status | Read Only | Boolean | B_DET_SVT_INTLK_IN_FLOW_STATUS | N/A | 65 | 1 | record (ai, "B_DET_SVT_INTLK_IN_FLOW_STATUS"){}
Sum of Coolant Outlet Flow Status | SVT EPICS Outlet Coolant Flow Status | Read Only | Boolean | B_DET_SVT_INTLK_OUT_FLOW_STATUS | N/A | 66 | 1 | record (ai, "B_DET_SVT_INTLK_OUT_FLOW_STATUS"){}
Sum of Coolant Temperature Status | SVT EPICS Coolant Temp Status | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_STATUS | N/A | 67 | 1 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_STATUS"){}
Sum of Coolant Leak Status | SVT EPICS Coolant Leak | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_STATUS | N/A | 68 | 1
Individual Sensor Latched Errors | SVT EPICS HFCB Temp R1 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_HI_ERR | N/A | 69 | 1 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_HI_ERR"){}
| SVT EPICS HFCB Temp R1 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_LO_ERR | N/A | 70 | 2 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_LATCHED_LO_ERR"){}
| SVT EPICS HFCB Temp R2 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_HI_ERR | N/A | 71 | 3 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_HI_ERR"){}
| SVT EPICS HFCB Temp R2 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_LO_ERR | N/A | 72 | 4 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_LATCHED_LO_ERR"){}
| SVT EPICS HFCB Temp R3 M1 Top Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_HI_ERR | N/A | 73 | 5 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_HI_ERR"){}
| SVT EPICS HFCB Temp R3 M1 Top Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_LO_ERR | N/A | 74 | 6 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_LATCHED_LO_ERR"){}
| SVT EPICS Detector Int Temp R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_HI_ERR | N/A | 75 | 7 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_HI_ERR"){}
| SVT EPICS Detector Int Temp R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_LO_ERR | N/A | 76 | 8 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_LATCHED_LO_ERR"){}
| SVT EPICS Detector Int Temp R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_HI_ERR | N/A | 77 | 9 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_HI_ERR"){}
| SVT EPICS Detector Int Temp R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_LO_ERR | N/A | 78 | 10 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Temp 1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_HI_ERR | N/A | 79 | 11 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Temp 1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_LO_ERR | N/A | 80 | 12 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Temp 2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_HI_ERR | N/A | 81 | 13 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Temp 2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_LO_ERR | N/A | 82 | 14 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_LATCHED_LO_ERR"){}
| SVT EPICS Det Internal Humidity R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_HI_ERR | N/A | 83 | 15 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_HI_ERR"){}
| SVT EPICS Det Internal Humidity R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_LO_ERR | N/A | 84 | 16 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_LATCHED_LO_ERR"){}
| SVT EPICS Det Internal Humidity R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_HI_ERR | N/A | 85 | 17 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_HI_ERR"){}
| SVT EPICS Det Internal Humidity R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_LO_ERR | N/A | 86 | 18 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_LATCHED_LO_ERR"){}
| SVT EPICS Det Internal Dew Point R2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_HI_ERR | N/A | 87 | 19 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_HI_ERR"){}
| SVT EPICS Det Internal Dew Point R2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_LO_ERR | N/A | 88 | 20 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_LATCHED_LO_ERR"){}
| SVT EPICS Det Internal Dew Point R3 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_HI_ERR | N/A | 89 | 21 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_HI_ERR"){}
| SVT EPICS Det Internal Dew Point R3 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_LO_ERR | N/A | 90 | 22 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Humidity H1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_HI_ERR | N/A | 91 | 23 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Humidity H1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_LO_ERR | N/A | 92 | 24 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Humidity H2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_HI_ERR | N/A | 93 | 25 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Humidity H2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_LO_ERR | N/A | 94 | 26 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Dew Point 1 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_HI_ERR | N/A | 95 | 27 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Dew Point 1 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_LO_ERR | N/A | 96 | 28 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_LATCHED_LO_ERR"){}
| SVT EPICS Ambient Dew Point 2 Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_HI_ERR | N/A | 97 | 29 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_HI_ERR"){}
| SVT EPICS Ambient Dew Point 2 Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_LO_ERR | N/A | 98 | 30 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_LATCHED_LO_ERR"){}
| SVT EPICS Outlet Coolant Flow Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_HI_ERR | N/A | 99 | 31 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_HI_ERR"){}
| SVT EPICS Outlet Coolant Flow Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_LO_ERR | N/A | 100 | 32 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_LATCHED_LO_ERR"){}
| SVT EPICS Inlet Coolant Flow Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_HI_ERR | N/A | 101 | 33 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_HI_ERR"){}
| SVT EPICS Inlet Coolant Flow Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_LO_ERR | N/A | 102 | 34 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_LATCHED_LO_ERR"){}
| SVT EPICS Coolant Temp Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_HI_ERR | N/A | 103 | 35 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_LATCHED_HI_ERR"){}
| SVT EPICS Coolant Temp Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_LO_ERR | N/A | 104 | 36 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_LATCHED_LO_ERR"){}
| SVT EPICS Coolant Leak Latched Hi Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LATCHED_HI_ERR | N/A | 105 | 37 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK_LATCHED_HI_ERR"){}
| SVT EPICS Coolant Leak Latched Lo Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LATCHED_LO_ERR | N/A | 106 | 38 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK_LATCHED_LO_ERR"){}
Sum of Temperature Latched Errors | SVT EPICS Temperature Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_TEMP_LATCHED_ERR | N/A | 107 | 1 | record (ai, "B_DET_SVT_INTLK_TEMP_LATCHED_ERR"){}
Sum of Humidity Latched Errors | SVT EPICS Humidity Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_HUMID_LATCHED_ERR | N/A | 108 | 1 | record (ai, "B_DET_SVT_INTLK_HUMID_LATCHED_ERR"){}
Sum of Dew Point Latched Errors | SVT EPICS Dew Point Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_DEWP_LATCHED_ERR | N/A | 109 | 1 | record (ai, "B_DET_SVT_INTLK_DEWP_LATCHED_ERR"){}
Sum Coolant Inlet Flow Latched Errors | SVT EPICS Inlet Coolant Flow Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_IN_FLOW_LATCHED_ERR | N/A | 110 | 1 | record (ai, "B_DET_SVT_INTLK_IN_FLOW_LATCHED_ERR"){}
Sum of Coolant Outlet Flow Latched Errors | SVT EPICS Outlet Coolant Flow Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_OUT_FLOW_LATCHED_ERR | N/A | 111 | 1 | record (ai, "B_DET_SVT_INTLK_OUT_FLOW_LATCHED_ERR"){}
Sum of Coolant Temperature Latched Errors | SVT EPICS Coolant Temperature Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_TEMP_LATCHED_ERR | N/A | 112 | 1 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_LATCHED_ERR"){}
Sum of Coolant Leak Latched Errors | SVT EPICS Coolant Leak Latched Error | Read Only | Boolean | B_DET_SVT_INTLK_COOL_LEAK_LATCHED_ERR | N/A | 113 | 1
Reset of All Latched Errors | SVT EPICS Reset Latched Errors | Read/Write | Boolean | B_DET_SVT_INTLK_RESET_LATCHED_ERR | N/A | 114 | 1 | record (ai, "B_DET_SVT_INTLK_RESET_LATCHED_ERR"){}
Individual Sensor Interlock Enables | SVT EPICS HFCB Temp R1 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R1_ENABLE | N/A | 115 | 1 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_ENABLE"){}
| SVT EPICS HFCB Temp R2 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R2_ENABLE | N/A | 116 | 2 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_ENABLE"){}
| SVT EPICS HFCB Temp R3 M1 Top Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_HFCB_TEMP_R3_ENABLE | N/A | 117 | 3 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_ENABLE"){}
| SVT EPICS Detector Int Temp R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_TEMP_R2_ENABLE | N/A | 118 | 4 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_ENABLE"){}
| SVT EPICS Detector Int Temp R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_TEMP_R3_ENABLE | N/A | 119 | 5 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_ENABLE"){}
| SVT EPICS Ambient Temp 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_TEMP1_ENABLE | N/A | 120 | 6 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_ENABLE"){}
| SVT EPICS Ambient Temp 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_TEMP2_ENABLE | N/A | 121 | 7 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_ENABLE"){}
| SVT EPICS Det Internal Humidity R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_HUMID_R2_ENABLE | N/A | 122 | 8 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_ENABLE"){}
| SVT EPICS Det Internal Humidity R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_HUMID_R3_ENABLE | N/A | 123 | 9 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_ENABLE"){}
| SVT EPICS Det Internal Dew Point R2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_DEWP_R2_ENABLE | N/A | 124 | 10 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_ENABLE"){}
| SVT EPICS Det Internal Dew Point R3 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_INT_DEWP_R3_ENABLE | N/A | 125 | 11 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_ENABLE"){}
| SVT EPICS Ambient Humidity H1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_HUMID1_ENABLE | N/A | 126 | 12 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_ENABLE"){}
| SVT EPICS Ambient Humidity H2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_HUMID2_ENABLE | N/A | 127 | 13 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_ENABLE"){}
| SVT EPICS Ambient Dew Point 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_DEWP1_ENABLE | N/A | 128 | 14 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_ENABLE"){}
| SVT EPICS Ambient Dew Point 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_AMB_DEWP2_ENABLE | N/A | 129 | 15 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_ENABLE"){}
| SVT EPICS Outlet Coolant Flow Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_OUT_FLOW_ENABLE | N/A | 130 | 16 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_ENABLE"){}
| SVT EPICS Inlet Coolant Flow Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_IN_FLOW_ENABLE | N/A | 131 | 17 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_ENABLE"){}
| SVT EPICS Coolant Temp Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_TEMP_ENABLE | N/A | 132 | 18 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_ENABLE"){}
| SVT EPICS Coolant Leak 1 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_LEAK1_ENABLE | N/A | 133 | 19 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK1_ENABLE"){}
| SVT EPICS Coolant Leak 2 Interlock Enable | Read/Write | Boolean | B_DET_SVT_INTLK_COOL_LEAK2_ENABLE | N/A | 134 | 20 | record (ai, "B_DET_SVT_INTLK_COOL_LEAK2_ENABLE"){}
Individual Sensor Threshold Controls | SVT EPICS HFCB Temp R1 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1_HI | °C | 135 | 1 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_HI"){}
| SVT EPICS HFCB Temp R1 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R1_LO | °C | 136 | 2 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R1_LO"){}
| SVT EPICS HFCB Temp R2 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2_HI | °C | 137 | 3 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_HI"){}
| SVT EPICS HFCB Temp R2 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R2_LO | °C | 138 | 4 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R2_LO"){}
| SVT EPICS HFCB Temp R3 M1 Top Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3_HI | °C | 139 | 5 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_HI"){}
| SVT EPICS HFCB Temp R3 M1 Top Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_HFCB_TEMP_R3_LO | °C | 140 | 6 | record (ai, "B_DET_SVT_INTLK_HFCB_TEMP_R3_LO"){}
| SVT EPICS Detector Int Temp R2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R2_HI | °C | 141 | 7 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_HI"){}
| SVT EPICS Detector Int Temp R2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R2_LO | °C | 142 | 8 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R2_LO"){}
| SVT EPICS Detector Int Temp R3 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R3_HI | °C | 143 | 9 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_HI"){}
| SVT EPICS Detector Int Temp R3 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_TEMP_R3_LO | °C | 144 | 10 | record (ai, "B_DET_SVT_INTLK_INT_TEMP_R3_LO"){}
| SVT EPICS Ambient Temp 1 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP1_HI | °C | 145 | 11 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_HI"){}
| SVT EPICS Ambient Temp 1 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP1_LO | °C | 146 | 12 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP1_LO"){}
| SVT EPICS Ambient Temp 2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP2_HI | °C | 147 | 13 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_HI"){}
| SVT EPICS Ambient Temp 2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_TEMP2_LO | °C | 148 | 14 | record (ai, "B_DET_SVT_INTLK_AMB_TEMP2_LO"){}
| SVT EPICS Det Internal Humidity R2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R2_HI | %RH | 149 | 15 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_HI"){}
| SVT EPICS Det Internal Humidity R2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R2_LO | %RH | 150 | 16 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R2_LO"){}
| SVT EPICS Det Internal Humidity R3 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R3_HI | %RH | 151 | 17 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_HI"){}
| SVT EPICS Det Internal Humidity R3 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_HUMID_R3_LO | %RH | 152 | 18 | record (ai, "B_DET_SVT_INTLK_INT_HUMID_R3_LO"){}
| SVT EPICS Ambient Humidity H1 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID1_HI | %RH | 153 | 19 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_HI"){}
| SVT EPICS Ambient Humidity H1 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID1_LO | %RH | 154 | 20 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID1_LO"){}
| SVT EPICS Ambient Humidity H2 Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID2_HI | %RH | 155 | 21 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_HI"){}
| SVT EPICS Ambient Humidity H2 Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_HUMID2_LO | %RH | 156 | 22 | record (ai, "B_DET_SVT_INTLK_AMB_HUMID2_LO"){}
| SVT EPICS Det Internal Dew Point R2 Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_DEWP_R2_THRES |  | 157 | 23 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R2_THRES"){}
| SVT EPICS Det Internal Dew Point R3 Threshold | Read/Write | Double | B_DET_SVT_INTLK_INT_DEWP_R3_THRES |  | 158 | 24 | record (ai, "B_DET_SVT_INTLK_INT_DEWP_R3_THRES"){}
| SVT EPICS Ambient Dew Point 1 Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_DEWP1_THRES |  | 159 | 25 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP1_THRES"){}
| SVT EPICS Ambient Dew Point 2 Threshold | Read/Write | Double | B_DET_SVT_INTLK_AMB_DEWP2_THRES |  | 160 | 26 | record (ai, "B_DET_SVT_INTLK_AMB_DEWP2_THRES"){}
| SVT EPICS Outlet Coolant Flow Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW_HI | L/Min | 161 | 27 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_HI"){}
| SVT EPICS Outlet Coolant Flow Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_OUT_FLOW_LO | L/Min | 162 | 28 | record (ai, "B_DET_SVT_INTLK_COOL_OUT_FLOW_LO"){}
| SVT EPICS Inlet Coolant Flow Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_IN_FLOW_HI | L/Min | 163 | 29 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_HI"){}
| SVT EPICS Inlet Coolant Flow Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_IN_FLOW_LO | L/Min | 164 | 30 | record (ai, "B_DET_SVT_INTLK_COOL_IN_FLOW_LO"){}
| SVT EPICS Coolant Temp Hi Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_TEMP_HI | °C | 165 | 31 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_HI"){}
| SVT EPICS Coolant Temp Lo Threshold | Read/Write | Double | B_DET_SVT_INTLK_COOL_TEMP_LO | °C | 166 | 32 | record (ai, "B_DET_SVT_INTLK_COOL_TEMP_LO "){}
Threshold Control Status | SVT EPICS Threshold Control | Read Only | Boolean | B_DET_SVT_INTLK_EPICS_THRESH_CTRL | N/A | 167 | 1 | record (ai, "B_DET_SVT_INTLK_EPICS_THRESH_CTRL"){}
Hardware Interlock Status | SVT EPICS Chiller Enable Status | Read Only | Boolean | B_DET_SVT_INTLK_CHILLER_ENABLE_STAT | N/A | 168 | 1 | record (ai, "B_DET_SVT_INTLK_CHILLER_ENABLE_STAT"){}
| SVT EPICS Chiller Override Status | Read Only | Boolean | B_DET_SVT_INTLK_CHILLER_OVERRIDE_STAT | N/A | 169 | 2 | record (ai, "B_DET_SVT_INTLK_CHILLER_OVERRIDE_STAT"){}
| SVT EPICS Mpod Enable Status | Read Only | Boolean | B_DET_SVT_INTLK_MPOD_ENABLE_STAT | N/A | 170 | 3 | record (ai, "B_DET_SVT_INTLK_MPOD_ENABLE_STAT"){}
| SVT EPICS Mpod Overide Status | Read Only | Boolean | B_DET_SVT_INTLK_MPOD_OVERRIDE_STAT | N/A | 171 | 5 | record (ai, "B_DET_SVT_INTLK_MPOD_OVERRIDE_STAT"){}
Interlock System Status | SVT EPICS cRIO Heartbeat | Read Only | Boolean | B_HW_SVTCRIO_HEARTBEAT | N/A | 172 | 1
| SVT EPICS cRIO CPU Usage | Read Only | Double | B_HW_SVTCRIO_CPULOAD | % | 173 | 2
| SVT EPICS System Uptime | Read Only | Double | B_HW_SVTCRIO_UPTIME | Sec | 174 | 3